## Cx Equip. Status COLP-1
#VALUE! | [6 empty] | COLP01 | Level 1 Report | Level 2 Test | Level 2 Report | Level 2 Tag | Level 3 Startup | Level 3 Report | Level 3 Tag | Level 4 FPT & SOO | Level 4 Report | Level 4 Tag
[7 empty] | Pending | 0 | 21 | 68 | 95 | 123 | 407 | 424 | 107 | 115 | 119
[7 empty] | In Progress | 1 | 45 | 112 | 0 | 256 | 112 | 3 | 12 | 28 | 0
Sify DC-T6 & T7- BOM 64 | [6 empty] | Completed | 418 | 609 | 495 | 570 | 251 | 110 | 198 | 24 | 0 | 24
Cx Equipment Status | [6 empty] | Skipped | 265 | 10 | 10 | 20 | 55 | 55 | 59 | 538 | 538 | 538
[7 empty] | % Pending | 0% | 3.111% | 10.07% | 14.29% | 19.52% | 64.71% | 67.84% | 74.83% | 80.42% | 83.22%
[7 empty] | % In Progress | 0.2387% | 6.667% | 16.59% | 0% | 40.63% | 17.81% | 0.48% | 8.392% | 19.58% | 0%
[7 empty] | % Completed | 99.76% | 90.22% | 73.33% | 85.71% | 39.84% | 17.49% | 31.68% | 16.78% | 0% | 16.78%
[7 empty] | Total | 419 | 675 | 675 | 665 | 630 | 629 | 625 | 143 | 143 | 143
Sl. No. | Equipment ID | FOK/ROK | Service | Location | Type | Capacity | Resposible Vendor | Level 1 Report | Level 2 Test | L2 Report | L2 Tag | Level 3 Startup | L3 Report | L3 Tag | Level 4 FPT | Level 4 Report | L4 Tag | Remarks | SCCS Verification | Remarks
E.001 | GIS-EXTN-SWITCHBOARD-T6 | FOK | Electrical | GF(L0) | GIS Extension Switchboard | 22KV | Siemens | 100% | 100% | 100% | 100% | 90% | 0% | 0% | x | x | x | MFM Verification completed without load. With load verification required, L3 Report Commented
E.002 | T6T7-EXTN-SWITCHBOARD-STBY | ROK | Electrical | GF(L0) | AIS Extension Switchboard | 22KV | Jyothi Switchgear | 100% | 100% | 100% | 100% | 90% | 20% | 0% | x | x | x | analog signal is pending in BMS
E.003 | GIS-EXTN-SWITCHBOARD-T7 | ROK | Electrical | GF(L0) | GIS Extension Switchboard | 22KV | Siemens | 100% | 100% | 100% | 100% | 90% | 0% | 0% | x | x | x | MFM Verification completed without load. With load verification required
E.004 | T6-CSHT-1 | ROK | Electrical | GF(L0) | HT Panel | 22kV | Siemens | 100% | 100% | 100% | 100% | 90% | 0% | 0% | x | x | x | MFM Verification completed without load. With load verification required
E.005 | T6-CSHT-2 | FOK | Electrical | GF(L0) | HT Panel | 22kV | Siemens | 100% | 100% | 100% | 100% | 90% | 0% | 0% | x | x | x | MFM Verification completed without load. With load verification required
E.006 | T7-CSHT-1 | FOK | Electrical | GF(L0) | HT Panel | 22kV | Siemens | 100% | 100% | 100% | 100% | 90% | 0% | 0% | x | x | x | MFM verification pending ( Fok Incomplete),Updated Drawing Pending
E.007 | T7-CSHT-2 | ROK | Electrical | GF(L0) | HT Panel | 22kV | Siemens | 100% | 100% | 100% | 100% | 90% | 0% | 0% | x | x | x | MFM Verification completed without load. With load verification required
E.008 | T6T7-RMU-19 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 100% | 100% | 99% | 0% | 0% | x | x | x | analog signal is pending
E.009 | T6T7-RMU-2 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 100% | 100% | 90% | 0% | 0% | x | x | x | analog signal is pending
E.010 | T6T7-RMU-35 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 100% | 100% | 90% | 0% | 0% | x | x | x | analog signal is pending
E.011 | T6T7-RMU-36 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 100% | 100% | 90% | 0% | 0% | x | x | x | analog signal is pending
E.012 | T6T7-RMU-43 | FOK | Electrical | GF(L0) | RMU | 22kV | Siemens | 100% | 100% | 100% | 100% | 90% | 50% | 0% | x | x | x | MFM Verification completed without load. With load verification required
E.013 | T6T7-RMU-29 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 100% | 100% | 90% | 0% | 0% | x | x | x | analog signal is pending in BMS
E.014 | T6T7-RMU-1 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 100% | 100% | 90% | 0% | 0% | x | x | x | analog signal is pending in BMS
E.015 | T6T7-RMU-15 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 100% | 100% | 90% | 0% | 0% | x | x | x | analog signal is pending in BMS
E.016 | T6T7-RMU-38 | ROK | Electrical | GF(L0) | RMU | 22kV | Siemens | 100% | 100% | 100% | 100% | 90% | 50% | 0% | x | x | x | MFM Verification completed without load. With load verification required
E.017 | T6T7-RMU-20 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 100% | 100% | 90% | 0% | 0% | x | x | x | analog signal is pending in BMS
E.018 | T6T7-RMU-5 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 100% | 100% | 90% | 0% | 0% | x | x | x | analog signal is pending in BMS
E.019 | T6T7-RMU-6 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 100% | 100% | 90% | 0% | 0% | x | x | x | analog signal is pending in BMS
E.020 | T6T7-RMU-46 | ROK | Electrical | GF(L0) | RMU | 22kV | Siemens | 100% | 100% | 100% | 100% | 90% | 50% | 0% | x | x | x | MFM Verification completed without load. With load verification required
E.021 | T6T7-RMU-47 | ROK | Electrical | GF(L0) | RMU | 22kV | Siemens | 100% | 100% | 100% | 100% | 90% | 50% | 0% | x | x | x | MFM Verification completed without load. With load verification required
E.022 | T6T7-RMU-3 | FOK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 100% | 100% | 90% | 0% | 0% | x | x | x | analog signal is pending in BMS
E.023 | T6T7-RMU-39 | ROK | Electrical | GF(L0) | RMU | 22kV | Siemens | 100% | 100% | 100% | 100% | 90% | 50% | 0% | x | x | x | MFM Verification completed without load. With load verification required
E.024 | T6T7-RMU-54 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 100% | 100% | 90% | 0% | 0% | x | x | x | analog signal is pending in BMS
E.025 | T6T7-TX-L7-1 | ROK | Electrical | GF(L0) | Dry type transformer | 2750KVA | Hitachi | 100% | 100% | 100% | 100% | 100% | 30% | 0% | x | x | x | Report pending from efficienergi
E.026 | T6T7-TX-L7-2 | ROK | Electrical | GF(L0) | Dry type transformer | 2750KVA | Hitachi | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | BMS Verification pending
E.027 | T6T7-TX-L7-3 | ROK | Electrical | GF(L0) | Dry type transformer | 2750KVA | Hitachi | 100% | 100% | 100% | 100% | 100% | 30% | 0% | x | x | x | Report pending from efficienergi
E.028 | T6T7-TX-L7-4 | ROK | Electrical | GF(L0) | Dry type transformer | 2750KVA | Hitachi | 100% | 100% | 100% | 100% | 100% | 30% | 0% | x | x | x | Report pending from efficienergi
E.029 | T6T7-TX-L7-5 | ROK | Electrical | GF(L0) | Dry type transformer | 2750KVA | Hitachi | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | BMS Verification pending
E.030 | T6T7-TX-CATCHER-C1 | ROK | Electrical | GF(L0) | Dry type transformer | 2750KVA | Hitachi | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | Report inprogress
E.031 | T6T7-TX-CATCHER-M1 | ROK | Electrical | GF(L0) | Dry type transformer | 2750KVA | Hitachi | 100% | 100% | 80% | 0% | 0% | 0% | 0% | x | x | x | Torque test is pending
E.032 | T6T7-TX-CATCHER-C2 | ROK | Electrical | GF(L0) | Dry type transformer | 2750KVA | Hitachi | 100% | 100% | 80% | 0% | 0% | 0% | 0% | x | x | x | Torque test pending
E.033 | T6T7-TX-CATCHER-M2 | ROK | Electrical | GF(L0) | Dry type transformer | 2750KVA | Hitachi | 100% | 100% | 80% | 0% | 0% | 0% | 0% | x | x | x | Torque test is pending
E.034 | T6T7-TX-RISER-2 | ROK | Electrical | GF(L0) | Dry type transformer | 2750KVA | Hitachi | 100% | 100% | 100% | 100% | 70% | 0% | 0% | x | x | x | BMS Verification pending
E.035 | T6T7-TX-CH-5 | ROK | Electrical | GF(L0) | Dry type transformer | 2750KVA | Hitachi | 100% | 100% | 100% | 100% | 100% | 30% | 0% | x | x | x | Report pending from efficienergi
E.036 | T6T7-TX-CH-9 | ROK | Electrical | GF(L0) | Dry type transformer | 2750KVA | Hitachi | 100% | 100% | 90% | 100% | 100% | 0% | 0% | x | x | x | Torque test is pending
E.037 | T6T7-TX-CH-2 | FOK | Electrical | GF(L0) | Dry type transformer | 2750KVA | Hitachi | 100% | 100% | 90% | 100% | 50% | 0% | 0% | x | x | x | BMS Verification pending
E.038 | T6T7-TX-CH-6 | ROK | Electrical | GF(L0) | Dry type transformer | 2750KVA | Hitachi | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | Reports under review ( inprogress)
E.039 | T6T7-TX-RISER-1 | ROK | Electrical | GF(L0) | Dry type transformer | 2750KVA | Hitachi | 100% | 100% | 100% | 100% | 100% | 30% | 0% | x | x | x | Report pending from efficienergi
E.040 | T6T7-TX-RISER-3 | ROK | Electrical | GF(L0) | Dry type transformer | 2750KVA | Hitachi | 100% | 100% | 100% | 100% | 100% | 30% | 0% | x | x | x | Report pending from efficienergi | Verified | OG to APFC Panel (630A CB) settings are pending, as the circuit breaker is currently discharged and has a digital display.
E.041 | T6T7-TX-RISER-4 | ROK | Electrical | GF(L0) | Dry type transformer | 2750KVA | Hitachi | 100% | 100% | 100% | 100% | 80% | 0% | 0% | x | x | x | BMS Verification pending | Verified | OG to APFC Panel (630A CB) settings are pending, as the circuit breaker is currently discharged and has a digital display.
E.042 | T6T7-LT-PANEL-L7-1 | ROK | Electrical | GF(L0) | LT Panel | 2750KVA | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 30% | 100% | x | x | x | Reports Comment raised (BMS Screenshot naming pending)
E.043 | T6T7-LT -PANEL-L7-2 | ROK | Electrical | GF(L0) | LT Panel | 2750KVA | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 30% | 100% | x | x | x | Reports Comment raised (BMS Screenshot naming pending)
E.044 | T6T7-LT-PANEL-L7-3 | ROK | Electrical | GF(L0) | LT Panel | 2750KVA | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 30% | 100% | x | x | x | Reports Comment raised (BMS Screenshot naming pending)
E.045 | T6T7-LT-PANEL-L7-4 | FOK | Electrical | GF(L0) | LT Panel | 2750KVA | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 30% | 100% | x | x | x | Reports Comment raised (BMS Screenshot naming pending)
E.046 | T6T7-LT PANEL-L7-5 | ROK | Electrical | GF(L0) | LT Panel | 2750KVA | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 30% | 100% | x | x | x | Reports Comment raised (BMS Screenshot naming pending)
E.047 | T6T7-TX PANEL -CHR-C1 | ROK | Electrical | GF(L0) | LT Panel | 2750KVA | Arrow Electricals | 100% | 100% | 100% | 100% | 50% | 0% | 0% | 0% | 0% | 0% | MFM Verification and TVSS Verification pending | Verified
E.048 | T6T7-TX PANEL -CHR-M1 | ROK | Electrical | GF(L0) | LT Panel | 2750KVA | Arrow Electricals | 100% | 100% | 100% | 100% | 50% | 0% | 0% | 0% | 0% | 0% |  | Verified
E.049 | T6T7-TX PANEL -CHR-C2 | FOK | Electrical | GF(L0) | LT Panel | 2750KVA | Arrow Electricals | 100% | 100% | 100% | 100% | 50% | 0% | 0% | 0% | 0% | 0% |  | Verified | OG to APFC Panel (630A CB) settings are pending, as the circuit breaker is currently discharged and has a digital display.
E.050 | T6T7-TX PANEL -CHR-M2 | ROK | Electrical | GF(L0) | LT Panel | 2750KVA | Arrow Electricals | 100% | 100% | 100% | 100% | 50% | 0% | 0% | 0% | 0% | 0% |  | Verified | OG to APFC Panel (630A CB) settings are pending, as the circuit breaker is currently discharged and has a digital display.
E.051 | T6T7-LT PNL-RISER-2 | ROK | Electrical | GF(L0) | LT Panel | 2750KVA | Arrow Electricals | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | BMS Verification pending
E.052 | T6T7-LT PNL-CH-2 | ROK | Electrical | GF(L0) | LT Panel | 2750KVA | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 30% | 100% | x | x | x | Reports Comment raised (BMS Screenshot naming pending)
E.053 | T6T7-LT PNL-CH-9 | ROK | Electrical | GF(L0) | LT Panel | 2750KVA | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 30% | 100% | x | x | x | Reports Comment raised (BMS Screenshot naming pending)
E.054 | T6T7-LT PNL-CH-5 | ROK | Electrical | GF(L0) | LT Panel | 2750KVA | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 30% | 100% | x | x | x | Reports Comment raised (BMS Screenshot naming pending) | Verified
E.055 | T6T7-LT PNL-CH-6 | ROK | Electrical | GF(L0) | LT Panel | 2750KVA | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 30% | 100% | x | x | x | Reports Comment raised (BMS Screenshot naming pending) | Verified
E.056 | T6T7-LT PNL-RISER-1 | ROK | Electrical | GF(L0) | LT Panel | 2750KVA | Arrow Electricals | 100% | 100% | 100% | 100% | 70% | 0% | 0% | x | x | x
E.057 | T6T7-TX PANEL RISER-3 | ROK | Electrical | GF(L0) | LT Panel | 2750KVA | Arrow Electricals | 100% | 100% | 100% | 100% | 70% | 0% | 0% | 0% | 0% | 0% | under review
E.058 | T6T7-TX PANEL RISER-4 | ROK | Electrical | GF(L0) | LT Panel | 2750KVA | Arrow Electricals | 100% | 100% | 100% | 100% | 70% | 0% | 0% | 0% | 0% | 0% | MFM checking pending
E.059 | APFC-PNL-CHR-C2 | ROK | Electrical | GF(L0) | LT Panel | 2750KVA | Listenlights | 100% | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x | CxL2 Report Pending From Vendor
E.060 | APFC-PNL-CHR-M2 | ROK | Electrical | GF(L0) | LT Panel | 2750KVA | Listenlights | 100% | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x | CXL2 Report Pending From Vendor
E.061 | APFC-PNL-RISER-3 | ROK | Electrical | GF(L0) | LT Panel | 2750KVA | Listenlights | 100% | 100% | 100% | 100% | 100% | 50% | 100% | x | x | x | CXL3 Report Pending From Vendor
E.062 | T6T7-RM-TX-RISER-4-L0 | ROK | Electrical | GF(L0) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 60% | 0% | 0% | x | x | x | BMS Verification pending
E.063 | T6T7-EDB-L/P-T7-L0-A1 | ROK | Electrical | GF(L0) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 60% | 0% | 0% | x | x | x | BMS Verification pending
E.064 | T6T7-DG-AUX-PANEL-T7-L0-1 | ROK | Electrical | GF(L0) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 60% | 0% | 0% | x | x | x | BMS Verification pending
E.065 | T6T7-EDB-L/P-T7-L0-A2 | ROK | Electrical | GF(L0) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 80% | 0% | 0% | x | x | x | BMS Verification pending
E.066 | T6T7-PAC-PANEL-T7-L0-A | ROK | Electrical | GF(L0) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 60% | 0% | 0% | x | x | x | BMS Verification pending
E.067 | T6T7-EDB-COMMON-SERVICES-PANEL-A2 | ROK | Electrical | GF(L0) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 80% | 100% | 80% | 0% | 0% | x | x | x | Report Comment Raised
E.068 | T6T7-EDB-L/P-T7-L0-B1 | ROK | Electrical | GF(L0) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x
E.069 | T6T7-DG-AUX-PANEL-T7-L0-2 | ROK | Electrical | GF(L0) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 80% | 0% | 0% | x | x | x | observation raised ( incomer 2 source is not available MFM verification is pending)
E.070 | T6T7-EDB-L/P-T7-L0-B2 | ROK | Electrical | GF(L0) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 80% | 100% | 100% | 0% | 0% | x | x | x | Report observation raised
E.071 | T6T7-PAC-PANEL-T7-L0-B | ROK | Electrical | GF(L0) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x
E.072 | T6T7-RM-TX-RISER-3-L0 | ROK | Electrical | GF(L0) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 60% | 0% | 0% | x | x | x | BMS Verification pending
E.073 | T6T7-EDB-L/P-T6-L0-A1 | ROK | Electrical | GF(L0) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 60% | 0% | 0% | x | x | x | BMS Verification pending
E.074 | T6T7-DG-AUX-PANEL-T6-L0-1 | ROK | Electrical | GF(L0) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 80% | 0% | 0% | x | x | x | observation raised ( incomer 2 source is not available MFM verification is pending)
E.075 | T6T7-EDB-L/P-T6-L0-A2 | ROK | Electrical | GF(L0) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 60% | 0% | 0% | x | x | x
E.076 | T6T7-EDB-COMMON-SERVICES-PANEL-A1 | ROK | Electrical | GF(L0) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 80% | 0% | 0% | x | x | x
E.077 | T6T7-PAC-PANEL-T6-L0-A | ROK | Electrical | GF(L0) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 60% | 0% | 0% | x | x | x | Report Comment Raised, BMS Verification pending
E.078 | T6T7-PAC-PANEL-T6-L0-B | ROK | Electrical | GF(L0) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x
E.079 | T6T7-MCC-PANEL-1 | ROK | Electrical | GF(L0) | LT Panel | 415V | Gmmco | 100% | 0% | 0% | 0% | 0% | 0% | 0% | x | x | x
E.080 | T6T7-RM-TX-CHR-C2-L0 | ROK | Electrical | GF(L0) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x
E.081 | T6T7-RM-TX-CHR-M2-L0 | ROK | Electrical | GF(L0) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x
E.082 | T6T7-EDB-L/P-T6-L0-B1 | ROK | Electrical | GF(L0) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x
E.083 | T6T7-EDB-L/P-T6-L0-B2 | ROK | Electrical | GF(L0) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 60% | 0% | 0% | x | x | x | BMS Verification pending
E.084 | T6T7-DG-AUX-PANEL-T6-L0-2 | ROK | Electrical | GF(L0) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 80% | 0% | 0% | x | x | x | observation raised ( incomer 2 source is not available MFM verification is pending)
E.085 | T6T7-MCC-PANEL-2 | ROK | Electrical | GF(L0) | LT Panel | 415V | Gmmco | 100% | 0% | 0% | 0% | 0% | 0% | 0% | x | x | x
E.086 | APFC-PNL-RISER-4 | ROK | Electrical | GF(L0) | LT Panel | 2750KVA | Listenlights | 100% | 100% | 100% | 100% | 100% | 50% | 100% | x | x | x | CXL3 Report Pending From Vendor
E.087 | T6T7-TX-Panel-L7-1 | FOK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 30% | 100% | 0% | 0% | 0% | Report Comment Raised ( Screenshots nameing is misssing & Updated Report are still Pending fron Effencienrgi) | Verified
E.088 | T6T7-TX-Panel-L7-2 | ROK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 30% | 100% | 0% | 0% | 0% | Report Comment Raised ( Screenshots nameing is misssing & Updated Report are still Pending fron Effencienrgi) | Verified
E.089 | T6T7-TX-Panel-L7-3 | ROK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 30% | 100% | 0% | 0% | 0% | Report Comment Raised ( Screenshots nameing is misssing & Updated Report are still Pending fron Effencienrgi) | Verified
E.090 | T6T7-TX-Panel-L7-4 | ROK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 30% | 100% | 0% | 0% | 0% | Report Comment Raised ( Screenshots nameing is misssing & Updated Report are still Pending fron Effencienrgi) | Verified
E.091 | T6T7-TX-Panel-L7-5 | ROK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 30% | 100% | 0% | 0% | 0% | Report Comment Raised ( Screenshots nameing is misssing & Updated Report are still Pending fron Effencienrgi) | Verified
E.092 | T6T7-TX-PANEL RISER-2 | FOK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 30% | 100% | 80% | 0% | 0% | Report Comment Raised ( Screenshots nameing is misssing & Updated Report are still Pending fron Effencienrgi) | Verified | OG to APFC Panel (630A CB) settings are pending, as the circuit breaker is currently discharged and has a digital display.
E.093 | T6T7-RM-TX-RISER-2-L7-A1 | ROK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 30% | 100% | x | x | x | Report Comment Raised ( Screenshots nameing is misssing & Updated Report are still Pending fron Effencienrgi)
E.094 | T6T7-EDB-L/P-L7-A1 | ROK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 30% | 100% | x | x | x | Report Comment Raised ( Screenshots nameing is misssing & Updated Report are still Pending fron Effencienrgi) | Verified | outgoing to MMR-UDU-L7A and Outgoing to MMR- UPS-A Feeders settings pending due to live operational status
E.095 | T6T7-EDB-L/P-L7-A3 | ROK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 30% | 100% | x | x | x | Report Comment Raised ( Screenshots nameing is misssing & Updated Report are still Pending fron Effencienrgi) | Verified
E.096 | T6T7-MMR-UDU-L7-A | ROK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 30% | 100% | 80% | 0% | 0% | Report Comment Raised ( Screenshots nameing is misssing & Updated Report are still Pending fron Effencienrgi) | Verified
E.097 | T6T7-MECH-UDU-L7-A1 | ROK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 30% | 100% | 0% | 0% | 0% | Report pending from efficienergi . Second source is not available | Verified
E.098 | T6T7-MECH-PANEL-L7-A1 | ROK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 70% | 0% | 0% | x | x | x | Report pending from efficienergi | Verified | Outgoing to T6T7-MECH-PNL-L7-A2 Settings implementation pending as the breaker is not operational and CB is having a digital display for implementation
E.099 | T6T7-MECH-PANEL-L7-A2 | ROK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 70% | 0% | 0% | x | x | x | Report pending from efficienergi
E.100 | T6T7-RM-TX-CHR-C2-L7-B1 | ROK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x
E.101 | T6T7-EDB-L/P-L7-B1 | ROK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x |  | Verified
E.102 | T6T7-MECH-UDU-L7-B1 | ROK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | power source not avaliavble | Verified
E.103 | T6T7-MECH-PANEL-L7-B1 | ROK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x | BMS verification pending | Verified | Outgoing 1 is pending , that feeder they will provide a loto.
E.104 | T6T7-MECH-PANEL-L7-B2 | ROK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x | BMS verification pending
E.105 | T6T7-MECH-PANEL-L7-B3 | ROK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x | BMS verification pending | Verified
E.106 | T6T7-MECH-PANEL-L7-B4 | ROK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x | BMS verification pending | Verified
E.107 | T6T7-EDB-L/P-L7-B3 | ROK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 30% | 100% | x | x | x | Report Comment Raised ( Screenshots nameing is misssing & Updated Report are still Pending fron Effencienrgi) | Verified
E.108 | T6T7-EDB-L/P-L7-B4 | ROK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 0% | 100% | x | x | x | Report Comment Raised ( Screenshots nameing is misssing & Updated Report are still Pending fron Effencienrgi) | Verified
E.109 | T6T7-EDB-PAHU-MMR-L7-B | ROK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 0% | 100% | x | x | x | Report Comment Raised ( Screenshots nameing is misssing & Updated Report are still Pending fron Effencienrgi) | Verified
E.110 | T6T7-RM-TX-CHR-M2-L7-B2 | ROK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x
E.111 | T6T7-EDB-L/P-L7-B2 | ROK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 80% | 0% | 0% | x | x | x | Report pending from efficienergi | Verified
E.112 | T6T7-MECH-UDU-L7-B2 | ROK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0% |  | Verified
E.113 | T6T7-RM-TX-RISER-1-L7-A2 | FOK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 0% | 100% | x | x | x | Report pending from efficienergi
E.114 | T6T7-EDB-L/P-L7-A2 | FOK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 0% | 100% | x | x | x | CXL3 Reports pending | Verified | Outgoing to MMR-UDU-L7-B AND Outgoing to MMR- UDU-L7-UPS -B are having live operational sta
E.115 | T6T7-EDB-L/P-L7-A4 | ROK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 90% | 0% | 100% | x | x | x | CxL3 Interlock Verification Pending due to second source not available, MFM Reverifation Required due to no proper reading showing in BMS, High Current THD Showing | Verified
E.116 | T6T7-EDB-PAHU-MMR-L7-A | ROK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 0% | 100% | x | x | x | Report not received | Verified
E.117 | T6T7-MMR-UDU-L7-B | FOK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 80% | 0% | 0% | Report not received ( FOK Complete)
E.118 | T6T7-MECH-UDU-L7-A2 | FOK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 0% | 0% | 0% | MFM Reverifation Required due to no proper reading showing in BMS, High Current THD Showing | Verified
E.119 | T6T7-MECH-PANEL-L7-A3 | FOK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 80% | 0% | 0% | x | x | x | Report Unber Review | Verified
E.120 | T6T7-MECH-PANEL-L7-A4 | ROK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 0% | 100% | x | x | x | CDU
E.121 | APFC-PNL-RISER-2 | ROK | Electrical | 7F(L7) | LT Panel | 415V | Listenlights | 100% | 100% | 100% | 100% | 100% | 50% | 100% | x | x | x | CXL3 Report Pending From Vendor
E.122 | T6T7-EDB-L/P-L7-A3-CO | ROK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x | IR value low | Verified
E.123 | T6T7-EDB-L/P-L7-A4-CO | ROK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x | IR Value Low | Verified
E.124 | T6T7-EDB-L/P-L7-B3-CO | ROK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x | IR value Low | Verified
E.125 | T6T7-EDB-L/P-L7-B4-CO | ROK | Electrical | 7F(L7) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x | IR value Low | Verified
E.126 | T6T7-RM-TX-RISER-2-TERR-A1 | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 40% | 0% | 0% | x | x | x
E.127 | T6T7-EDB-L/P-TERR-A1 | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | (MFM verification and TVSS status was pending and field side points are pending) | Verified
E.128 | T6T7-EDB-L/P-TERR-A3 | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 0% | 0% | x | x | x | Reports pending | Verified
E.129 | T6T7-RM-TX-RISER-1-TERR-A2 | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 40% | 0% | 0% | x | x | x
E.130 | T6T7-EDB-L/P-TERR-A2 | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 40% | 0% | 0% | x | x | x |  | Verified | OG to CHILLER-3 settings are pending due to Live operational status
E.131 | T6T7-EDB-L/P-TERR-A4 | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | BMS Pending | Verified
E.132 | T6T7-EDB-L/P-TERR-B1 | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x | Not offered FOR Observation Closure | Verified
E.133 | T6T7-EDB-L/P-TERR-B3 | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 0% | 0% | x | x | x | Reports pending | Verified
E.134 | T6T7-EDB-L/P-TERR-B2 | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | BMS Pending | Verified
E.135 | T6T7-EDB-L/P-TERR-B4 | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 75% | 0% | 0% | x | x | x | Field side points need to be close (feeder missing tags need to be provide and drawing need to be change in current panel conditions Reports pending | Verified
E.136 | T6T7-PUMP-PANEL-TERR-A1 | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | 100% | 90% | 100% | 0% | 0% | 0% | 0% | x | x | x | Not offered FOR Observation Closure | Verified | Both the Incomer Cb's, Short time disable feature not available
E.137 | T6T7-PUMP-PANEL-TERR-B1 | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | 100% | 90% | 100% | 0% | 0% | 0% | 0% | x | x | x | Not offered FOR Observation Closure | Verified | Both the Incomer Cb's, Short time disable feature not available
E.138 | T6T7-TX-PANEL-CH2 | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 50% | 0% | 0% | 0% | 0% | 0% | Observation Raised (BMS TVSS, MFM verification pending , 2. BMS incomer 2 incoming-side indication is showing grey/disabled. Please check the issue and rectify it | Verified
E.139 | T6T7-CHSB-CH-2A | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 80% | 0% | 0% | x | x | x | BMS MFM Verification was pending | Verified
E.140 | T6T7-TX-PANEL-CH9 | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 50% | 0% | 0% | 0% | 0% | 0% | Observation Raised (BMS TVSS, MFM verification pending , 2. BMS incomer 2 incoming-side indication is showing grey/disabled. Please check the issue and rectify it | Verified
E.141 | T6T7-CHSB-CH-9A | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 80% | 0% | 0% | x | x | x | BMS MFM Verification was pending | Verified
E.142 | RM-TX-CHR-M2-TERR-T6-B2 | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 0% | 0% | x | x | x | Report pending from vendor
E.143 | RM-TX-CHR-C2-TERR-T6-B2 | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 0% | 0% | x | x | x | Reports pending From vendor
E.144 | CHSB-CH-2B | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 80% | 0% | 0% | x | x | x | BMS MFM Verification was pending | Verified
E.145 | CHSB-CH-9B | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 80% | 0% | 0% | x | x | x | BMS MFM Verification was pending | Verified
E.146 | T6T7-TX-PANEL-CH5 | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 70% | 0% | 0% | 0% | 0% | 0% | MFM Verification pending | Verified
E.147 | T6T7-CHSB-CH-5A | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 70% | 0% | 0% | x | x | x | MFM Verification pending | Verified
E.148 | T6T7-TX-PANEL-CH6 | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 90% | 0% | 0% | 0% | 0% | 0% | MFM Verification Pending. | Verified
E.149 | T6T7-CHSB-CH-6A | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 90% | 0% | 0% | x | x | x | BMS MFM Verification was pending | Verified
E.150 | RM-TX-CHR-M2-TERR-T7-B2 | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 0% | 0% | x | x | x | Reports pending From vendor
E.151 | RM-TX-CHR-C2-TERR-T7-B2 | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 0% | 0% | x | x | x | Reports pending From vendor
E.152 | CHSB-CH-5B | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 80% | 0% | 0% | x | x | x | BMS MFM Verification was pending | Verified
E.153 | CHSB-CH-6B | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 0% | 0% | x | x | x | Reports pending | Verified
E.154 | RM-TX-CHR-C2-TERR-T6-B1 | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 80% | 0% | 0% | x | x | x | Observation Raised
E.155 | RM-TX-CHR-M2-TERR-T6-B1 | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 80% | 0% | 0% | x | x | x | Observation Raised
E.156 | T6T7-CHSB-CH-6A | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | x | x | x | x | x | x | x | x | x | x
E.157 | RM-TX-CHR-C2-TERR-T7-B1 | ROK | Electrical | Terrace | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 100% | 0% | 0% | x | x | x | Reports pending From vendor
E.158 | T6T7-TX PANEL RISER-1 | ROK | Electrical | 6F(L6) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 50% | 0% | 0% | 80% | 0% | 0% | BMS Verification pending
E.159 | APFC-PNL-RISER-1 | ROK | Electrical | 6F(L6) | LT Panel | 415V | Orbittal | 100% | 100% | 100% | 100% | 100% | 0% | 0% | x | x | x | Report Pending From Vendor
E.160 | T6T7-RM-TX-RISER-1-L6-A2 | ROK | Electrical | 6F(L6) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | BMS Verification pending
E.161 | T6T7-EDB-L/P-L6-A2 | ROK | Electrical | 6F(L6) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | BMS Verification pending
E.162 | T6T7-EDB-L/P-L6-A4-CO | ROK | Electrical | 6F(L6) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x
E.163 | T6T7-EDB-L/P-L6-A4 | ROK | Electrical | 6F(L6) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 90% | 0% | 0% | x | x | x | Observation raised (Cx-L3)
E.164 | T6T7-BMS-UDU-L6-A | ROK | Electrical | 6F(L6) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 50% | 0% | 0% | 0% | 0% | 0% | BMS Verification pending
E.165 | T6T7-BMS-PANEL-L6-A | ROK | Electrical | 6F(L6) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | BMS Verification pending
E.166 | T6T7-RM-TX-CHR-M2-L6-B2 | ROK | Electrical | 6F(L6) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x | observation raised BBT termination pending
E.167 | T6T7-EDB-L/P-L6-B2 | ROK | Electrical | 6F(L6) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x | observation raised
E.168 | T6T7-PUMP-UDU-L6-B2 | ROK | Electrical | 6F(L6) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
E.169 | T6T7-BMS-PANEL-L6-B | ROK | Electrical | 6F(L6) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x
E.170 | T6T7-RM-TX-CHR-C2-L6-B1 | ROK | Electrical | 6F(L6) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x
E.171 | T6T7-EDB-L/P-L6-B1 | ROK | Electrical | 6F(L6) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x
E.172 | T6T7-PUMP-UDU-L6-B1 | ROK | Electrical | 6F(L6) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | Observation raised
E.173 | T6T7-BMS-UDU-L6-B | ROK | Electrical | 6F(L6) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | under review
E.174 | T6T7-RM-TX-RISER-2-L6-A1 | ROK | Electrical | 6F(L6) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | BMS verification Pending
E.175 | T6T7-EDB-L/P-L6-A1 | ROK | Electrical | 6F(L6) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 90% | 0% | 0% | x | x | x | Obserbvation raised (CX-L3)
E.176 | T6T7-PUMP-UDU-L6-A1 | ROK | Electrical | 6F(L6) | LT Panel | 415V | Arrow Electricals | 100% | 90% | 100% | 0% | 50% | 0% | 0% | 0% | 0% | 0% | BMS verification Pending
E.177 | T6T7-EDB-L/P-L6-A3-CO | ROK | Electrical | 6F(L6) | LT Panel | 415V | Arrow Electricals | 100% | 80% | 60% | 0% | 0% | 0% | 0% | x | x | x | outgoing termination pending/ Secondary injection report is pending
E.178 | T6T7-EDB-L/P-L6-A3 | ROK | Electrical | 6F(L6) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | observation rised (Cx-L3)
E.179 | T6T7-EL-UDU-L6-A1 | ROK | Electrical | 6F(L6) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 100% | 100% | 50% | 0% | 0% | 0% | 0% | 0% | BMS verification Pending
E.180 | T6T7-EL-UDU-L6-A2 | ROK | Electrical | 6F(L6) | LT Panel | 415V | Arrow Electricals | 100% | 100% | 75% | 100% | 50% | 0% | 0% | 0% | 0% | 0% | under review
E.181 | BMS & CONTROL UPS-A | ROK | Electrical | 6F(L6) | UPS | 400KVA | Riello | 100% | 100% | 100% | 100% | 100% | 30% | 0% | x | x | x | Reports Observation Raised
E.182 | SEC-PUMP-UPS-B2 | ROK | Electrical | 6F(L6) | UPS | 600KVA | Riello | 100% | 100% | 100% | 100% | 100% | 30% | 0% | x | x | x | Reports Observation Raised
E.183 | SEC-PUMP-UPS-B1 | ROK | Electrical | 6F(L6) | UPS | 600KVA | Riello | 100% | 100% | 100% | 100% | 100% | 30% | 0% | x | x | x | Reports Observation Raised
E.184 | SEC-PUMP-UPS-A1 | ROK | Electrical | 6F(L6) | UPS | 600KVA | Riello | 100% | 100% | 100% | 100% | 100% | 30% | 0% | x | x | x | Reports Observation Raised
E.185 | EL-UPS-A1 | ROK | Electrical | 6F(L6) | UPS | 100 KVA | Riello | 100% | 100% | 100% | 100% | 100% | 30% | 0% | x | x | x | Reports Observation Raised
E.186 | EL-UPS-A2 | ROK | Electrical | 6F(L6) | UPS | 100 KVA | Riello | 100% | 100% | 100% | 100% | 100% | 30% | 0% | x | x | x | Reports Observation Raised
E.187 | T6T7-DG PNL-RISER-1 | FOK | Electrical | DG Stack Area | DG Isolator Panel | 415V | Gmmco | 100% | 100% | 100% | 100% | 70% | 0% | 0% | x | x | x | Obsrvation Raised,BMS Pending
E.188 | T6T7-DG PNL-L7-1 | ROK | Electrical | DG Stack Area | DG Isolator Panel | 415V | Gmmco | 100% | 100% | 0% | 0% | 70% | 0% | 0% | x | x | x | Obsrvation Raised,BMS Pending
E.189 | T6T7-DG PNL-L7-2 | ROK | Electrical | DG Stack Area | DG Isolator Panel | 415V | Gmmco | 100% | 100% | 0% | 0% | 70% | 0% | 0% | x | x | x | Obsrvation Raised,BMS Pending
E.190 | T6T7-DG PNL-L7-3 | ROK | Electrical | DG Stack Area | DG Isolator Panel | 415V | Gmmco | 100% | 100% | 100% | 0% | 70% | 0% | 0% | x | x | x | Obsrvation Raised,BMS Pending
E.191 | T6T7-DG PNL-L7-4 | ROK | Electrical | DG Stack Area | DG Isolator Panel | 415V | Gmmco | 100% | 100% | 100% | 0% | 70% | 0% | 0% | x | x | x | Obsrvation Raised,BMS Pending
E.192 | T6T7-DG PNL-L7-5 | ROK | Electrical | DG Stack Area | DG Isolator Panel | 415V | Gmmco | 100% | 70% | 0% | 0% | 70% | 0% | 0% | x | x | x | IR,HV Test,Stability test pending.(As Previously Discussed with Sify team,Mail Approval is Required)
E.193 | T6T7-DG PNL -CATCHER-C1 | ROK | Electrical | DG Stack Area | DG Isolator Panel | 415V | Gmmco | 100% | 100% | 100% | 0% | 70% | 0% | 0% | x | x | x | Obsrvation Raised,BMS Pending
E.194 | T6T7-DG PNL -CATCHER-M1 | ROK | Electrical | DG Stack Area | DG Isolator Panel | 415V | Gmmco | 100% | 100% | 100% | 0% | 70% | 0% | 0% | x | x | x | Obsrvation Raised,BMS Pending
E.195 | T6T7-DG PNL-CATCHER-C2 | ROK | Electrical | DG Stack Area | DG Isolator Panel | 415V | Gmmco | 100% | 90% | 90% | 0% | 60% | 0% | 0% | x | x | x | Obsrvation Raised,BMS Pending
E.196 | T6T7-DG PNL -CATCHER-M2 | ROK | Electrical | DG Stack Area | DG Isolator Panel | 415V | Gmmco | 100% | 100% | 100% | 0% | 70% | 0% | 0% | x | x | x | Observation raised
E.197 | T6T7-DG PNL-RISER-2 | ROK | Electrical | DG Stack Area | DG Isolator Panel | 415V | Gmmco | 100% | 100% | 100% | 100% | 70% | 0% | 0% | x | x | x | Obsrvation Raised,BMS Pending
E.198 | T6T7-DG PNL-CH-2 | ROK | Electrical | DG Stack Area | DG Isolator Panel | 415V | Gmmco | 100% | 100% | 100% | 0% | 70% | 0% | 0% | x | x | x | Obsrvation Raised,BMS Pending
E.199 | T6T7-DG PNL-CH-9 | ROK | Electrical | DG Stack Area | DG Isolator Panel | 415V | Gmmco | 100% | 100% | 100% | 0% | 70% | 0% | 0% | x | x | x | Obsrvation Raised,BMS Pending
E.200 | T6T7-DG PNL-CH-5 | ROK | Electrical | DG Stack Area | DG Isolator Panel | 415V | Gmmco | 100% | 100% | 100% | 0% | 70% | 0% | 0% | x | x | x | Obsrvation Raised,BMS Pending
E.201 | T6T7-DG PNL-CH-6 | ROK | Electrical | DG Stack Area | DG Isolator Panel | 415V | Gmmco | 100% | 100% | 100% | 0% | 70% | 0% | 0% | x | x | x | Obsrvation Raised,BMS Pending
E.202 | T6T7-DG-PNL-RISER-3 | ROK | Electrical | DG Stack Area | DG Isolator Panel | 415V | Gmmco | 100% | 100% | 100% | 0% | 70% | 0% | 0% | x | x | x | P2P checklist is pending , to be provided by 26-08-2026
E.203 | T6T7-DG-PNL-RISER-4 | ROK | Electrical | DG Stack Area | DG Isolator Panel | 415V | Gmmco | 100% | 100% | 100% | 0% | 70% | 0% | 0% | x | x | x | Obsrvation Raised,BMS Pending
E.204 | T6T7-DG-RISER-1 | FOK | Electrical | DG Stack Area | DG | 3000KVA | Gmmco | 100% | 100% | 100% | 100% | 70% | 0% | 0% | x | x | x | Obsrvation Raised,BMS Pending
E.205 | T6T7-DG-L7-1 | ROK | Electrical | DG Stack Area | DG | 3000KVA | Gmmco | 100% | 100% | 0% | 0% | 80% | 0% | 0% | x | x | x | Obsrvation Raised,BMS Pending, Report not received
E.206 | T6T7-DG-L7-2 | ROK | Electrical | DG Stack Area | DG | 3000KVA | Gmmco | 100% | 100% | 0% | 0% | 80% | 0% | 0% | x | x | x | Obsrvation Raised,BMS Pending, Report not received
E.207 | T6T7-DG-L7-3 | ROK | Electrical | DG Stack Area | DG | 3000KVA | Gmmco | 100% | 100% | 100% | 0% | 80% | 0% | 0% | x | x | x | Obsrvation Raised,BMS Pending
E.208 | T6T7-DG-L7-4 | ROK | Electrical | DG Stack Area | DG | 3000KVA | Gmmco | 100% | 100% | 100% | 0% | 80% | 0% | 0% | x | x | x | Obsrvation Raised,BMS Pending
E.209 | T6T7-DG-L7-5 | ROK | Electrical | DG Stack Area | DG | 3000KVA | Gmmco | 100% | 100% | 0% | 0% | 80% | 0% | 0% | x | x | x | Report not received
E.210 | T6T7-DG -CATCHER-C1 | ROK | Electrical | DG Stack Area | DG | 3000KVA | Gmmco | 100% | 100% | 100% | 0% | 80% | 0% | 0% | x | x | x | Obsrvation Raised,BMS Pending
E.211 | T6T7-DG -CATCHER-M1 | ROK | Electrical | DG Stack Area | DG | 3000KVA | Gmmco | 100% | 100% | 100% | 0% | 80% | 0% | 0% | x | x | x | Obsrvation Raised,BMS Pending
E.212 | T6T7-DG -CATCHER-C2 | ROK | Electrical | DG Stack Area | DG | 3000KVA | Gmmco | 100% | 100% | 100% | 0% | 80% | 0% | 0% | x | x | x | Obsrvation Raised,BMS Pending
E.213 | T6T7-DG -CATCHER-M2 | ROK | Electrical | DG Stack Area | DG | 3000KVA | Gmmco | 100% | 100% | 100% | 0% | 80% | 0% | 0% | x | x | x | visual inspection chceks & design verification is pending.
E.214 | T6T7-DG -RISER-2 | ROK | Electrical | DG Stack Area | DG | 3000KVA | Gmmco | 100% | 100% | 100% | 100% | 80% | 0% | 0% | x | x | x | Obsrvation Raised,BMS Pending
E.215 | T6T7-DG-CH-2 | ROK | Electrical | DG Stack Area | DG | 3000KVA | Gmmco | 100% | 100% | 100% | 0% | 80% | 0% | 0% | x | x | x | Obsrvation Raised,BMS Pending
E.216 | T6T7-DG-CH-9 | ROK | Electrical | DG Stack Area | DG | 3000KVA | Gmmco | 100% | 100% | 100% | 0% | 80% | 0% | 0% | x | x | x | Obsrvation Raised,BMS Pending
E.217 | T6T7-DG-CH-5 | ROK | Electrical | DG Stack Area | DG | 3000KVA | Gmmco | 100% | 100% | 100% | 0% | 80% | 0% | 0% | x | x | x | Obsrvation Raised,BMS Pending/RCA
E.218 | T6T7-DG-CH-6 | ROK | Electrical | DG Stack Area | DG | 3000KVA | Gmmco | 100% | 100% | 100% | 0% | 80% | 0% | 0% | x | x | x | Obsrvation Raised,BMS Pending
E.219 | T6T7-DG-RISER-3 | ROK | Electrical | DG Stack Area | DG | 3000KVA | Gmmco | 100% | 100% | 100% | 0% | 80% | 0% | 0% | x | x | x | Obsrvation Raised,BMS Pending
E.220 | T6T7-DG-RISER-4 | ROK | Electrical | DG Stack Area | DG | 3000KVA | Gmmco | 100% | 100% | 100% | 0% | 80% | 0% | 0% | x | x | x | Obsrvation Raised,BMS Pending
E.221 | MMR UPS-A | FOK | Electrical | 7F(L7) | UPS | 600KVA | Riello | 100% | 100% | 100% | 100% | 100% | 30% | 0% | x | x | x | Reports Observation Raised
E.222 | MECH-L7-UPS-A1 | ROK | Electrical | 7F(L7) | UPS | 400KVA | Riello | 100% | 100% | 100% | 100% | 100% | 30% | 0% | x | x | x | Reports Observation Raised
E.223 | MECH-L7-UPS-B1 | ROK | Electrical | 7F(L7) | UPS | 400KVA | Riello | 100% | 100% | 100% | 100% | 100% | 30% | 0% | x | x | x | Reports Observation Raised
E.224 | MECH-L7-UPS-B2 | ROK | Electrical | 7F(L7) | UPS | 400KVA | Riello | 100% | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x
E.225 | MMR UPS-B | ROK | Electrical | 7F(L7) | UPS | 600KVA | Riello | 100% | 100% | 100% | 100% | 100% | 30% | 0% | x | x | x | Reports Observation Raised
E.226 | MECH-L7-UPS-A2 | FOK | Electrical | 7F(L7) | UPS | 400KVA | Riello | 100% | 100% | 100% | 100% | 100% | 30% | 0% | x | x | x | Reports Observation Raised
E.227 | (T6T7-PDU)L7-MMR-YZ1-A | ROK | Electrical | 7F(L7) | PDU | 300 KVA | Delta | 100% | 100% | 100% | 100% | 100% | 80% | 0% | x | x | x | BCPM BMS Screenshots needs to be shared for the L3 Report closure
E.228 | (T6T7-PDU)L7-MMR-YZ2-A | ROK | Electrical | 7F(L7) | PDU | 300 KVA | Delta | 100% | 100% | 100% | 100% | 100% | 80% | 0% | x | x | x | BCPM BMS Screenshots needs to be shared for the L3 Report closure
E.229 | (T6T7-PDU)L7-MMR-YZ1-B | FOK | Electrical | 7F(L7) | PDU | 300 KVA | Delta | 100% | 100% | 100% | 100% | 100% | 80% | 0% | x | x | x | BCPM BMS Screenshots needs to be shared for the L3 Report closure
E.230 | (T6T7-PDU)L7-MMR-YZ2-B | ROK | Electrical | 7F(L7) | PDU | 300 KVA | Delta | 100% | 100% | 100% | 100% | 100% | 80% | 0% | x | x | x | BCPM BMS Screenshots needs to be shared for the L3 Report closure
E.231 | RPP-L7-1 | FOK | Electrical | 7F(L7) | RPP | 1000A | ABB | 100% | 100% | 100% | 100% | 70% | 0% | 0% | x | x | x | CxL3 initiated. Mains & Catcher C1 Source is available other M1 source is pending,BCPM Test inprogress,
E.232 | RPP-L7-2 | ROK | Electrical | 7F(L7) | RPP | 1000A | ABB | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | CxL3 initiated. Mains & Catcher C1 Source is available other M1 source is pending,BMS not verified.
E.233 | RPP-L7-3 | ROK | Electrical | 7F(L7) | RPP | 1000A | ABB | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | CxL3 initiated. Mains & Catcher C1 Source is available other M1 source is pending,BMS not verified.
E.234 | RPP-L7-4 | ROK | Electrical | 7F(L7) | RPP | 1000A | ABB | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | CxL3 initiated. Mains & Catcher C1 Source is available other M1 source is pending,BMS not verified.
E.235 | RPP-L7-5 | ROK | Electrical | 7F(L7) | RPP | 1000A | ABB | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | CxL3 initiated. Mains & Catcher C1 Source is available other M1 source is pending,BMS not verified.
E.236 | RPP-L7-6 | ROK | Electrical | 7F(L7) | RPP | 1000A | ABB | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | CxL3 initiated. Mains & Catcher C1 Source is available other M1 source is pending,BMS not verified.
E.237 | RPP-L7-7 | ROK | Electrical | 7F(L7) | RPP | 1000A | ABB | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | CxL3 initiated. Mains & Catcher C1 Source is available other M1 source is pending,BMS not verified.
E.238 | RPP-L7-8 | ROK | Electrical | 7F(L7) | RPP | 1000A | ABB | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | CxL3 initiated. Mains & Catcher C1 Source is available other M1 source is pending,BMS not verified.
E.239 | RPP-L7-9 | ROK | Electrical | 7F(L7) | RPP | 1000A | ABB | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | CxL3 initiated. Mains & Catcher C1 Source is available other M1 source is pending,BMS not verified.
E.240 | RPP-L7-10 | ROK | Electrical | 7F(L7) | RPP | 1000A | ABB | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | CxL3 initiated. Mains & Catcher C1 Source is available other M1 source is pending,BMS not verified.
E.241 | RPP-L7-11 | ROK | Electrical | 7F(L7) | RPP | 1000A | ABB | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | CxL3 initiated. Mains & Catcher C1 Source is available other M1 source is pending,BMS not verified.
E.242 | RPP-L7-12 | ROK | Electrical | 7F(L7) | RPP | 1000A | ABB | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | CxL3 initiated. Mains & Catcher C1 Source is available other M1 source is pending,BMS not verified.
E.243 | RPP-L7-13 | ROK | Electrical | 7F(L7) | RPP | 1000A | ABB | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | CxL3 initiated. Mains & Catcher C1 Source is available other M1 source is pending,BMS not verified.
E.244 | RPP-L7-14 | ROK | Electrical | 7F(L7) | RPP | 1000A | ABB | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | CxL3 initiated. Mains & Catcher C1 Source is available other M1 source is pending,BMS not verified.
E.245 | RPP-L7-15 | ROK | Electrical | 7F(L7) | RPP | 1000A | ABB | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | CxL3 initiated. Mains & Catcher C1 Source is available other M1 source is pending,BMS not verified.
E.246 | RPP-L7-16 | ROK | Electrical | 7F(L7) | RPP | 1000A | ABB | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | CxL3 initiated. Mains & Catcher C1 Source is available other M1 source is pending,BMS not verified.
E.247 | RPP-L7-17 | ROK | Electrical | 7F(L7) | RPP | 1000A | ABB | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | CxL3 initiated. Mains & Catcher C1 Source is available other M1 source is pending,BMS not verified.
E.248 | RPP-L7-18 | ROK | Electrical | 7F(L7) | RPP | 1000A | ABB | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | CxL3 initiated. Mains & Catcher C1 Source is available other M1 source is pending,BMS not verified.
E.249 | RPP-L7-19 | ROK | Electrical | 7F(L7) | RPP | 1000A | ABB | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | CxL3 initiated. Mains & Catcher C1 Source is available other M1 source is pending,BMS not verified.
E.250 | RPP-L7-20 | ROK | Electrical | 7F(L7) | RPP | 1000A | ABB | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | CxL3 initiated. Mains & Catcher C1 Source is available other M1 source is pending,BMS not verified.
E.251 | RPP-L7-21 | ROK | Electrical | 7F(L7) | RPP | 1000A | ABB | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | CxL3 initiated. Mains & Catcher C1 Source is available other M1 source is pending,BMS not verified.
E.252 | RPP-L7-22 | ROK | Electrical | 7F(L7) | RPP | 1000A | ABB | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | CxL3 initiated. Mains & Catcher C1 Source is available other M1 source is pending,BMS not verified.
E.253 | RPP-L7-23 | ROK | Electrical | 7F(L7) | RPP | 1000A | ABB | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | CxL3 initiated. Mains & Catcher C1 Source is available other M1 source is pending,BMS not verified.
E.254 | RPP-MCCP | ROK | Electrical | 7F(L7) | RPP | - | ABB | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | BMS verification Pending
E.255 | HT CABLE | ROK | Electrical |  | CABLE |  |  | x | 100% | 80% | x | x | x | x | x | x | x
E.256 | LT CABLE | ROK | Electrical |  | CABLE |  |  | x | 80% | 80% | x | x | x | x | x | x | x
E255 | T6T7-BBT | ROK | Electrical |  | BBT |  | Dhupar brothers | x | 60% | 60% | x | 60% | 15% | x | x | x | x
M.241 | Electrical SOO | ROK | Electrical | - | Electrical SOO | - | - | x | x | x | x | x | x | x | 0% | 0% | 0%
F.072 | WLD-7F | FOK | ELV | 7F(L7) | WLD | - | Douse Fire | x | 70% | 0% | 0% | 0% | 0% | 0% | x | x | x | WLD master panel verification is pending, sensing cable installation is pending
F.074 | T6T7-PAC-PNL-T6-L0-A-BMS-RIO-1 | ROK | ELV | GF(L0) | BMS RIO | - | Mitsubishi | x | 100% | 100% | 100% | 90% | 0% | 100% | x | x | x | Conditional tag provided since point to point verification is in progress
F.075 | T6T7-EDB-COM-SER-PNL-A1-BMS-RIO-2 | FOK | ELV | GF(L0) | BMS RIO | - | Mitsubishi | x | 100% | 100% | 100% | 90% | 0% | 100% | x | x | x | Conditional tag provided since point to point verification is in progress
F.076 | T6T7-PAC-PNL-T6-L0-B-BMS-RIO-3 | ROK | ELV | GF(L0) | BMS RIO | - | Mitsubishi | x | 100% | 100% | 100% | 90% | 0% | 100% | x | x | x | Conditional tag provided since point to point verification is in progress
F.077 | T6T7-DG-AUX-PNL-T6-L0-2-BMS RIO-4 | ROK | ELV | GF(L0) | BMS RIO | - | Mitsubishi | x | 100% | 100% | 100% | 90% | 0% | 100% | x | x | x | Conditional tag provided since point to point verification is in progress
F.078 | T6T7-PAC-PNL-T7-L0-A-BMS-RIO-5 | ROK | ELV | GF(L0) | BMS RIO | - | Mitsubishi | x | 100% | 100% | 100% | 90% | 0% | 100% | x | x | x | Conditional tag provided since point to point verification is in progress
F.079 | T6T7-EDB-L/P-T7-L0-A2-PNL-BMS-RIO-6 | ROK | ELV | GF(L0) | BMS RIO | - | Mitsubishi | x | 100% | 100% | 100% | 90% | 0% | 100% | x | x | x | Conditional tag provided since point to point verification is in progress
F.080 | T6T7-PAC-PNL-T7-L0-B-BMS-RIO-7 | ROK | ELV | GF(L0) | BMS RIO | - | Mitsubishi | x | 100% | 100% | 100% | 90% | 0% | 100% | x | x | x | Conditional tag provided since point to point verification is in progress
F.081 | T6T7-DG-AUX-PNL-T7-L0-2-BMS-RIO-8 | ROK | ELV | GF(L0) | BMS RIO | - | Mitsubishi | x | 100% | 100% | 100% | 90% | 0% | 100% | x | x | x | Conditional tag provided since point to point verification is in progress
F.082 | T6T7-EDB-L/P-L7-A4-BMS-RIO-01 | FOK | ELV | 7F(L7) | BMS RIO | - | Mitsubishi | x | 100% | 100% | 100% | 100% | 50% | 100% | x | x | x | Updated Drawing , power failure on the BMS shows a delay exceeding 60 seconds, T+RH Sensor calliberation pending.
F.083 | T6T7-MECH-PNL-L7-B3-BMS-RIO-02 | ROK | ELV | 7F(L7) | BMS RIO | - | Mitsubishi | x | 100% | 100% | 100% | 100% | 50% | 100% | x | x | x | Updated Drawing , power failure on the BMS shows a delay exceeding 60 seconds, T+RH Sensor calliberation pending.
F.084 | T6T7-MECH-PNL-L7-A4-BMS-RIO-03 | ROK | ELV | 7F(L7) | BMS RIO | - | Mitsubishi | x | 100% | 100% | 100% | 100% | 50% | 100% | x | x | x | Updated Drawing , power failure on the BMS shows a delay exceeding 60 seconds, T+RH Sensor calliberation pending.
F.085 | T6T7-MECH-PNL-L7-B4-BMS-RIO-04 | ROK | ELV | 7F(L7) | BMS RIO | - | Mitsubishi | x | 100% | 100% | 100% | 100% | 50% | 100% | x | x | x | Updated Drawing , power failure on the BMS shows a delay exceeding 60 seconds, T+RH Sensor calliberation pending.
F.086 | T6T7-MECH-PNL-L7-A2-BMS-RIO-05 | ROK | ELV | 7F(L7) | BMS RIO | - | Mitsubishi | x | 100% | 100% | 100% | 100% | 50% | 100% | x | x | x | Updated Drawing , power failure on the BMS shows a delay exceeding 60 seconds, T+RH Sensor calliberation pending.
F.087 | T6T7-MECH-PNL-L7-B1-BMS-RIO-06 | ROK | ELV | 7F(L7) | BMS RIO | - | Mitsubishi | x | 100% | 100% | 100% | 100% | 50% | 100% | x | x | x | Updated Drawing , power failure on the BMS shows a delay exceeding 60 seconds, T+RH Sensor calliberation pending.
F.088 | T6T7-EDB-L/P-L7-A3-BMS-RIO-7 | ROK | ELV | 7F(L7) | BMS RIO | - | Mitsubishi | x | 100% | 100% | 100% | 100% | 50% | 100% | x | x | x | Updated Drawing , power failure on the BMS shows a delay exceeding 60 seconds, T+RH Sensor calliberation pending.
F.089 | T6T7-TF-BMS-A-RIO-1 | FOK | ELV | Terrace | BMS RIO | - | Mitsubishi | x | 100% | 80% | 100% | 70% | 0% | 0% | x | x | x
F.090 | T6T7-TF-BMS-B-RIO-2 | ROK | ELV | Terrace | BMS RIO | - | Mitsubishi | x | 100% | 80% | 100% | 70% | 0% | 0% | x | x | x
F.091 | T6T7-BMS-M-CPU-L0/TF-A-SYS | FOK | ELV | GF(L0) | BMS PLC | - | Mitsubishi | x | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x | Updated Drawing and cable Schedule
F.092 | T6T7-BMS-M-CPU-L0/TF-B-SYS | ROK | ELV | GF(L0) | BMS PLC | - | Mitsubishi | x | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x | Updated Drawing and cable Schedule
F.093 | T6T7-BMS-M-CPU-L7-A-SYS | FOK | ELV | 7F(L7) | BMS PLC | - | Mitsubishi | x | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x | Updated Drawing and cable Schedule
F.094 | T6T7-BMS-M-CPU-L7-B-SYS | ROK | ELV | 7F(L7) | BMS PLC | - | Mitsubishi | x | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x | Updated Drawing and cable Schedule,Controller serial no missing
F.095 | T6/T7-TF-BMS-RM-A-PLC-A | FOK | ELV | Terrace | BMS PLC | - | Mitsubishi | x | 80% | 0% | 0% | 0% | 0% | 0% | x | x | x | Observations are raised.
F.096 | T6/T7-TF-BMS-RM-B-PLC-B | ROK | ELV | Terrace | BMS PLC | - | Mitsubishi | x | 80% | 0% | 0% | 0% | 0% | 0% | x | x | x | Power cable termination is pending.
F.097 | T6-7-HSD-PLC-1 | FOK | ELV | GF(L0) | HSD Automation System | - | GMMCO | x | 75% | 0% | 0% | 0% | 0% | 0% | x | x | x
F.098 | T6-7-HSD-PLC-2 | ROK | ELV | GF(L0) | HSD Automation System | - | GMMCO | x | 75% | 0% | 0% | 0% | 0% | 0% | x | x | x
F.099 | T6-7-DG Building RIO Panel - 1 | FOK | ELV | DG Building | HSD Automation System | - | GMMCO | x | 0% | 0% | 0% | 0% | 0% | 0% | x | x | x | Removed from Tracker
F.100 | T6-7-DG Building RIO Panel - 2 | ROK | ELV | DG Building | HSD Automation System | - | GMMCO | x | 0% | 0% | 0% | 0% | 0% | 0% | x | x | x | Removed from Tracker
F.101 | T6-7-HSD-Northeast RIO Panel-1 | FOK | ELV | GF(L0) | HSD Automation System | - | GMMCO | x | 75% | 0% | 0% | 0% | 0% | 0% | x | x | x
F.102 | T6-7-HSD-Northeast RIO Panel-2 | ROK | ELV | GF(L0) | HSD Automation System | - | GMMCO | x | 75% | 0% | 0% | 0% | 0% | 0% | x | x | x
F.103 | T6-7-HSD-Southeast RIO Panel-1 | ROK | ELV | 3F(L3) | HSD Automation System | - | GMMCO | x | 75% | 0% | 0% | 0% | 0% | 0% | x | x | x
F.104 | T6-7-HSD-Southeast RIO Panel-2 | ROK | ELV | 3F(L3) | HSD Automation System | - | GMMCO | x | 75% | 0% | 0% | 0% | 0% | 0% | x | x | x
F.105 | T6-7-HSD-Southwest RIO Panel-1 | ROK | ELV | 3F(L3) | HSD Automation System | - | GMMCO | x | 75% | 0% | 0% | 0% | 0% | 0% | x | x | x
F.106 | T6-7-HSD-Southwest RIO Panel-2 | ROK | ELV | 3F(L3) | HSD Automation System | - | GMMCO | x | 75% | 0% | 0% | 0% | 0% | 0% | x | x | x
F.107 | T6-7-HSD-Northwest RIO Panel-1 | ROK | ELV | 3F(L3) | HSD Automation System | - | GMMCO | x | 75% | 0% | 0% | 0% | 0% | 0% | x | x | x
F.108 | T6-7-HSD-Northwest RIO Panel-2 | ROK | ELV | 3F(L3) | HSD Automation System | - | GMMCO | x | 100% | 80% | 100% | 0% | 0% | 0% | x | x | x
F.109 | CPM PLC -1 | FOK | ELV | TF(L9) | CPM PLC | - | Mitsubishi | x | 100% | 80% | 100% | 0% | 0% | 0% | x | x | x | Not offered
F.110 | CPM Common RIO-1 | ROK | ELV | TF(L9) | CPM RIO | - | Mitsubishi | x | 100% | 80% | 100% | 0% | 0% | 0% | x | x | x
F.111 | CPM Common RIO-2 | ROK | ELV | TF(L9) | CPM RIO | - | Mitsubishi | x | 100% | 80% | 100% | 0% | 0% | 0% | x | x | x
F.112 | Chiller RIO Panel -01 | FOK | ELV | TF(L9) | CPM RIO | - | Mitsubishi | x | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x | L2 REPORT Ravi 29-07 (EOD)
F.113 | Chiller RIO Panel -02 | ROK | ELV | TF(L9) | CPM RIO | - | Mitsubishi | x | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x | L2 REPORT Ravi 29-07 (EOD)
F.114 | Chiller RIO Panel -03 | ROK | ELV | TF(L9) | CPM RIO | - | Mitsubishi | x | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x | L2 REPORT Ravi 29-07 (EOD)
F.115 | Chiller RIO Panel -04 | ROK | ELV | TF(L9) | CPM RIO | - | Mitsubishi | x | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x | L2 REPORT Ravi 29-07 (EOD)
F.116 | Max Cool Panel | FOK | ELV | 7F(L7) | Max Cool | - | Trinitytouch | x | 100% | 100% | 100% | 100% | 60% | 99% | x | x | x | Report work done. CX alloy open issue, Maxcool CxL3 - In power failure scenario power restore maxcool communication has loss. MaxCool Panel 1 - DH sensor failure verification is pending.
F.140 | FLD-TP-01 | ROK | ELV | 8F(L8) | Fuel Leak Detection | - | Douse Fire | x | 0% | 0% | 0% | 0% | 0% | 0% | x | x | x
F.146 | LC WLD (LCMP) | FOK | ELV | 7F(L7) | LC WLD | - | ELSA | x | 50% | 0% | 0% | 0% | 0% | 0% | x | x | x | Panel section checked, Sensor Installtion is pending due to room radiness pending.
F.001 | FAS 1 | FOK | Fire | 7F(L7) | FAS | - | Douse Fire | x | 100% | 100% | 100% | 100% | 99% | 100% | x | x | x | L3 SS under review - and upload by - 09-09-2026 - NV5
F.002 | PAS 1 | FOK | Fire | 7F(L7) | PAS | - | Douse Fire | x | 100% | 100% | 100% | 100% | 99% | 100% | x | x | x | L3 SS under review - and upload by - 09-09-2026 - NV5
F.003 | FAS 1 | ROK | Fire | GF(L0) | FAS | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 99% | x | x | x | P2P checklist is pending from the Vendor CxL3, BMS SS pending , Conditional tag provided.
F.004 | PAS 1 | ROK | Fire | GF(L0) | PAS | - | Douse Fire | x | 100% | 100% | 100% | 100% | 80% | 99% | x | x | x | P2P checklist is pending from the Vendor CxL3
F.005 | FAS 1 | ROK | Fire | TF(L9) | FAS | - | Douse Fire | x | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x
F.006 | PAS 1 | ROK | Fire | TF(L9) | PAS | - | Douse Fire | x | 100% | 99% | 100% | 50% | 0% | 0% | x | x | x | 08-09-2026 - NV5 to be upload
F.009 | Pre Action Panel -L7-01 | ROK | Fire | 7F(L7) | Preaction System | - | Douse Fire | 100% | 100% | 100% | 100% | 100% | 99% | 0% | x | x | x | L2 - Pressure monitoring is pending, As discussed with Sify PMS is comman for entritre building and this will not be ready colp wise, so this will be completed after entire building rediness, Once tjis section is filled with this comments report can be uploaded L3 - Nitrogen purity test pending and Air test pending, Electrical parameter pending due to availibility of waeter, fault verification partially completed, SS report is pending with the vendor
F.010 | Pre Action Panel -L7-02 | FOK | Fire | 7F(L7) | Preaction System | - | Douse Fire | 100% | 100% | 100% | 100% | 100% | 99% | 0% | x | x | x | L2 - Pressure monitoring is pending, As discussed with Sify PMS is comman for entritre building and this will not be ready colp wise, so this will be completed after entire building rediness, Once tjis section is filled with this comments report can be uploaded L3 - Nitrogen purity test pending and Air test pending, Electrical parameter pending due to availibility of waeter, fault verification partially completed, SS report is pending with the vendor
F.011 | Pre Action Panel -L7-03 | ROK | Fire | 7F(L7) | Preaction System | - | Douse Fire | 100% | 100% | 100% | 100% | 100% | 99% | 100% | x | x | x | L2 - Pressure monitoring is pending, As discussed with Sify PMS is comman for entritre building and this will not be ready colp wise, so this will be completed after entire building rediness, Once tjis section is filled with this comments report can be uploaded L3 - Nitrogen purity test pending and Air test pending, Electrical parameter pending due to availibility of waeter, fault verification partially completed, SS report is pending with the vendor
F.012 | Pre Action Panel -L7-04 | ROK | Fire | 7F(L7) | Preaction System | - | Douse Fire | 100% | 100% | 100% | 100% | 100% | 99% | 100% | x | x | x | L2 - Pressure monitoring is pending, As discussed with Sify PMS is comman for entritre building and this will not be ready colp wise, so this will be completed after entire building rediness, Once tjis section is filled with this comments report can be uploaded L3 - Nitrogen purity test pending and Air test pending, Electrical parameter pending due to availibility of waeter, fault verification partially completed, SS report is pending with the vendor
F.013 | HSSD-L7-1 | ROK | Fire | 7F(L7) | Vesda | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x
F.014 | HSSD-L7-2 | ROK | Fire | 7F(L7) | Vesda | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x
F.015 | HSSD-L7-3 | ROK | Fire | 7F(L7) | Vesda | - | Douse Fire | x | 100% | 100% | 100% | 100% | 0% | 0% | x | x | x | Cx L3 BMS Screenshot Reports under review
F.016 | HSSD-L7-4 | ROK | Fire | 7F(L7) | Vesda | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x
F.017 | HSSD-L7-5 | ROK | Fire | 7F(L7) | Vesda | - | Douse Fire | x | 100% | 100% | 100% | 100% | 0% | 0% | x | x | x | Cx L3 BMS Screenshot Reports under review
F.018 | HSSD-L7-6 | ROK | Fire | 7F(L7) | Vesda | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x
F.019 | HSSD-L7-7 | ROK | Fire | 7F(L7) | Vesda | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x
F.020 | HSSD-L7-8 | FOK | Fire | 7F(L7) | Vesda | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x
F.021 | HSSD-L7-9 | ROK | Fire | 7F(L7) | Vesda | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x
F.022 | HSSD-L7-10 | ROK | Fire | 7F(L7) | Vesda | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x
F.023 | HSSD-L7-11 | ROK | Fire | 7F(L7) | Vesda | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x
F.024 | HSSD-L7-12 | ROK | Fire | 7F(L7) | Vesda | - | Douse Fire | x | 100% | 100% | 100% | 100% | 0% | 100% | x | x | x | Cx L3 BMS Screenshot Reports under review
F.025 | HSSD-L7-13 | ROK | Fire | 7F(L7) | Vesda | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x
F.026 | HSSD-L7-14 | ROK | Fire | 7F(L7) | Vesda | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x
F.027 | HSSD-L7-15 | ROK | Fire | 7F(L7) | Vesda | - | Douse Fire | x | 100% | 100% | 100% | 100% | 0% | 100% | x | x | x | Cx L3 BMS Screenshot Reports under review
F.028 | HSSD-L7-16 | ROK | Fire | 7F(L7) | Vesda | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x
F.029 | HSSD-L0-01 | ROK | Fire | GF(L0) | Vesda | - | Douse Fire | x | 100% | 100% | 100% | 100% | 80% | 0% | x | x | x | Cx Completed. BMS Screenshot report pending
F.030 | HSSD-L0-02 | ROK | Fire | GF(L0) | Vesda | - | Douse Fire | x | 100% | 100% | 100% | 100% | 80% | 0% | x | x | x | Cx Completed. BMS Screenshot report pending
F.031 | HSSD-L0-03 | ROK | Fire | GF(L0) | Vesda | - | Douse Fire | x | 100% | 100% | 100% | 100% | 80% | 0% | x | x | x | Cx Completed. BMS Screenshot report pending
F.032 | HSSD-L0-04 | ROK | Fire | GF(L0) | Vesda | - | Douse Fire | x | 100% | 100% | 100% | 100% | 80% | 0% | x | x | x | Cx Completed. BMS Screenshot report pending
F.033 | HSSD-L0-05 | ROK | Fire | GF(L0) | Vesda | - | Douse Fire | x | 100% | 100% | 100% | 100% | 80% | 0% | x | x | x | Cx Completed. BMS Screenshot report pending
F.034 | HSSD-L0-06 | ROK | Fire | GF(L0) | Vesda | - | Douse Fire | x | 100% | 100% | 100% | 100% | 80% | 0% | x | x | x | Cx Completed. BMS Screenshot report pending
F.035 | HSSD-L0-07 | ROK | Fire | GF(L0) | Vesda | - | Douse Fire | x | 100% | 100% | 100% | 100% | 80% | 0% | x | x | x | Cx Completed. BMS Screenshot report pending
F.036 | HSSD-L0-08 | ROK | Fire | GF(L0) | Vesda | - | Douse Fire | x | 100% | 100% | 100% | 100% | 80% | 0% | x | x | x | Cx Completed. BMS Screenshot report pending
F.037 | GSS BATTERY ROOM- T6-L7-A1 | FOK | Fire | 7F(L7) | Gas Supression System | - | Douse Fire | 100% | 100% | 100% | 100% | 100% | 99% | 100% | x | x | x | BMS screenshot report is pending from the vendor, recieved 10-08-2026
F.038 | GSS BATTERY ROOM- T6-L7-A2 | ROK | Fire | 7F(L7) | Gas Supression System | - | Douse Fire | 100% | 100% | 100% | 100% | 100% | 99% | 100% | x | x | x | BMS screenshot report is pending from the vendor
F.039 | GSS BATTERY ROOM- T6-L7-B1 | ROK | Fire | 7F(L7) | Gas Supression System | - | Douse Fire | 100% | 100% | 100% | 100% | 100% | 99% | 100% | x | x | x | BMS screenshot report is pending from the vendor
F.040 | GSS BATTERY ROOM- T6-L7-B2 | ROK | Fire | 7F(L7) | Gas Supression System | - | Douse Fire | 100% | 100% | 100% | 100% | 100% | 99% | 100% | x | x | x | BMS screenshot report is pending from the vendor
F.041 | GSS ELECT-UPS-ROOM-T6-L7-A1 | ROK | Fire | 7F(L7) | Gas Supression System | - | Douse Fire | 100% | 100% | 100% | 100% | 100% | 99% | 100% | x | x | x | BMS screenshot report is pending from the vendor
F.042 | GSS ELECT-UPS-ROOM-T6-L7-A2 | ROK | Fire | 7F(L7) | Gas Supression System | - | Douse Fire | 100% | 100% | 100% | 100% | 100% | 99% | 100% | x | x | x | BMS screenshot report is pending from the vendor
F.043 | GSS ELECT-UPS-ROOM-T6-L7-B1 | ROK | Fire | 7F(L7) | Gas Supression System | - | Douse Fire | 100% | 100% | 100% | 100% | 100% | 99% | 100% | x | x | x | BMS screenshot report is pending from the vendor |  |  | BMS screenshot report is pending from the vendor
F.044 | GSS ELECT-UPS-ROOM-T6-L7-B2 | ROK | Fire | 7F(L7) | Gas Supression System | - | Douse Fire | 100% | 100% | 100% | 100% | 100% | 99% | 100% | x | x | x
F.045 | GSS ELECT-UPS-ROOM-T7-L7-A1 | ROK | Fire | 7F(L7) | Gas Supression System | - | Douse Fire | 100% | 100% | 100% | 100% | 100% | 99% | 100% | x | x | x | BMS screenshot report is pending from the vendor
F.046 | GSS ELECT-UPS-ROOM-T7-L7-A2 | ROK | Fire | 7F(L7) | Gas Supression System | - | Douse Fire | 100% | 100% | 100% | 100% | 100% | 99% | 100% | x | x | x | BMS screenshot report is pending from the vendor
F.047 | GSS ELECT-UPS-ROOM-T7-L7-B1 | ROK | Fire | 7F(L7) | Gas Supression System | - | Douse Fire | 100% | 100% | 100% | 100% | 100% | 99% | 100% | x | x | x | BMS screenshot report is pending from the vendor
F.048 | GSS ELECT-UPS-ROOM-T7-L7-B2 | ROK | Fire | 7F(L7) | Gas Supression System | - | Douse Fire | 100% | 100% | 100% | 100% | 100% | 99% | 100% | x | x | x | BMS screenshot report is pending from the vendor
F.049 | GSS BMS ROOM-TERR-A | ROK | Fire | TF(L9) | Gas Supression System | - | Douse Fire | 100% | 100% | 99% | 100% | 100% | 0% | 0% | x | x | x | Pipework Visual Inspection Checks and Pressure testing completed, reports pending BMS screensshots report to be shared by the vendor
F.050 | GSS BMS ROOM-TERR-B | ROK | Fire | TF(L9) | Gas Supression System | - | Douse Fire | 100% | 100% | 99% | 100% | 100% | 0% | 0% | x | x | x | Pipework Visual Inspection Checks and Pressure testing completed, reports pending BMS screensshots report to be shared by the vendor
F.051 | RRP-L7-01 | ROK | Fire | 7F(L7) | Rodent Repellent System | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Checklist Appendix pending- CxL3
F.052 | RRP-L7-02 | ROK | Fire | 7F(L7) | Rodent Repellent System | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Checklist Appendix pending- CxL3
F.053 | RRP-L7-03 | ROK | Fire | 7F(L7) | Rodent Repellent System | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Checklist Appendix pending- CxL3
F.054 | RRP-L7-04 | ROK | Fire | 7F(L7) | Rodent Repellent System | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Checklist Appendix pending- CxL3
F.055 | RRP-L7-05 | ROK | Fire | 7F(L7) | Rodent Repellent System | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Checklist Appendix pending- CxL3
F.056 | RRP-L7-06 | ROK | Fire | 7F(L7) | Rodent Repellent System | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Checklist Appendix pending- CxL3
F.057 | RRP-L7-07 | ROK | Fire | 7F(L7) | Rodent Repellent System | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Checklist Appendix pending- CxL3
F.058 | RRP-L7-08 | ROK | Fire | 7F(L7) | Rodent Repellent System | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Checklist Appendix pending- CxL3
F.059 | RRP-L7-09 | ROK | Fire | 7F(L7) | Rodent Repellent System | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Checklist Appendix pending- CxL3
F.060 | RRP-L7-10 | ROK | Fire | 7F(L7) | Rodent Repellent System | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Checklist Appendix pending- CxL3
F.061 | RRP-L0-01 | ROK | Fire | GF(L0) | Rodent Repellent System | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | CxL3 Report checklist pending
F.062 | RRP-L0-02 | ROK | Fire | GF(L0) | Rodent Repellent System | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Checklist Appendix pending- CxL3
F.063 | RRP-L0-03 | ROK | Fire | GF(L0) | Rodent Repellent System | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | CxL3 Report checklist pending
F.064 | RRP-L0-04 | ROK | Fire | GF(L0) | Rodent Repellent System | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Checklist Appendix pending- CxL3
F.065 | RRP-L0-05 | ROK | Fire | GF(L0) | Rodent Repellent System | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Checklist Appendix pending- CxL3
F.066 | RRP-L0-06 | ROK | Fire | GF(L0) | Rodent Repellent System | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Transducer installation is pending
F.067 | RRP-L0-07 | ROK | Fire | GF(L0) | Rodent Repellent System | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | CxL3 Report checklist pending
F.068 | RRP-L0-08 | ROK | Fire | GF(L0) | Rodent Repellent System | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Checklist Appendix pending- CxL3
F.069 | RRP-L0-09 | ROK | Fire | GF(L0) | Rodent Repellent System | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | CxL3 Report checklist pending
F.070 | RRP-L0-10 | ROK | Fire | GF(L0) | Rodent Repellent System | - | Douse Fire | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | CxL3 Report checklist pending
F.071 | RRP-TF-01 | ROK | Fire | TF(L9) | Rodent Repellent System | - | Douse Fire | x | 100% | 100% | 100% | 100% | 0% | 0% | x | x | x | P2P checklist is pending , Lift lobby 2 & 7 transducer need to be fixed.
F.138 | LINEAR HEAT DETECTION PANEL-1 | ROK | Fire | GF(L0) | Linear Heat Detection |  | Douse Fire |  | 100% | 100% | 100% | 70%
F.137 | LINEAR HEAT DETECTION PANEL-2 | ROK | Fire | GF(L0) | Linear Heat Detection | - | Douse Fire | x | 100% | 100% | 100% | 70% | 0% | 0% | x | x | x
F.139 | Linear Heat Detection | ROK | Fire | Terrace | Linear Heat Detection | - | Douse Fire | x | x | x | x | x | x | x | x | x | x
F.141 | FP-01 | ROK | Fire | Pump Room | Diesel Driven Pump | 2850 LPM | Listenlights | 100% | 100% | 0% | 100% | 0% | 0% | 0% | X | X | X
F.142 | FP-02 | ROK | Fire | Pump Room | Main Hydrant Pump | 2850 LPM | Listenlights | 100% | 100% | 0% | 100% | 0% | 0% | 0% | X | X | X
F.143 | FP-03 | ROK | Fire | Pump Room | Hydrant Jockey Pump | 180 LPM | Listenlights | 100% | 100% | 0% | 100% | 0% | 0% | 0% | X | X | X
F.144 | FP-04 | ROK | Fire | Pump Room | Main Sprinkler Pump | 2850 LPM | Listenlights | 100% | 100% | 0% | 100% | 0% | 0% | 0% | X | X | X
F.145 | FP-05 | ROK | Fire | Pump Room | Sprinkler Jockey Pump | 180 LPM | Listenlights | 100% | 100% | 0% | 100% | 0% | 0% | 0% | X | X | X
M.242 | Fire C&E Verification | FOK | Fire | - | Fire C&E Verification | - | - | x | x | x | x | x | x | x | 0% | 0% | 0%
F.117 | WMS -T6T7-L0 - 1 | FOK | Fire | GF(L0) | Water Mist System | - | Fogtech | x | 100% | 50% | 100% | 80% | 0% | 0% | x | x | x | Panel section checked, Sensor Installtion is pending due to room radiness pending.
F.118 | WMS -T6T7-L0 - 2 | ROK | Fire | GF(L0) | Water Mist System | - | Fogtech | x | 100% | 50% | 100% | 80% | 0% | 0% | x | x | x | Pressure test completed and Panel side CX l2 checks pending due to non readiness and till =date not offered
F.119 | WMS -T6T7-L0 - 3 | ROK | Fire | GF(L0) | Water Mist System | - | Fogtech | x | 100% | 50% | 100% | 80% | 0% | 0% | x | x | x | Pressure test completed and Panel side CX l2 checks pending due to non readiness and till =date not offered
F.120 | WMS -T6T7-L0 - 4 | ROK | Fire | GF(L0) | Water Mist System | - | Fogtech | x | 100% | 50% | 100% | 80% | 0% | 0% | x | x | x | Pressure test completed and Panel side CX l2 checks pending due to non readiness and till =date not offered
F.121 | WMS -T6T7-DG-L7-1 | ROK | Fire | DG Stack Area | Water Mist System | - | Fogtech | x | 100% | 50% | 100% | 0% | 0% | 0% | x | x | x
F.122 | WMS- T6T7-DG-L7-2 | ROK | Fire | DG Stack Area | Water Mist System | - | Fogtech | x | 100% | 50% | 100% | 100% | 0% | 0% | x | x | x | Pressure test completed and Panel side CX l2 checks pending due to non readiness and till =date not offered
F.123 | WMS- T6T7-DG-L7-3 | ROK | Fire | DG Stack Area | Water Mist System | - | Fogtech | x | 100% | 50% | 100% | 100% | 0% | 0% | x | x | x | Pressure test completed and Panel side CX l2 checks pending due to non readiness and till =date not offered
F.124 | WMS- T6T7-DG-L7-4 | ROK | Fire | DG Stack Area | Water Mist System | - | Fogtech | x | 100% | 50% | 100% | 0% | 0% | 0% | x | x | x | Pressure test completed and Panel side CX l2 checks pending due to non readiness and till =date not offered
F.125 | WMS- T6T7-DG-L7-5 | ROK | Fire | DG Stack Area | Water Mist System | - | Fogtech | x | 100% | 50% | 100% | 0% | 0% | 0% | x | x | x | Pressure test completed and Panel side CX l2 checks pending due to non readiness and till =date not offered
F.126 | WMS- T6T7-DG -CATCHER-C1 | ROK | Fire | DG Stack Area | Water Mist System | - | Fogtech | x | 100% | 50% | 100% | 100% | 0% | 0% | x | x | x
F.127 | WMS- T6T7-DG -CATCHER-M1 | ROK | Fire | DG Stack Area | Water Mist System | - | Fogtech | x | 100% | 50% | 100% | 0% | 0% | 0% | x | x | x | Pressure test completed and Panel side CX l2 checks pending due to non readiness and till =date not offered
F.128 | WMS- T6T7-DG -CATCHER-C2 | ROK | Fire | DG Stack Area | Water Mist System | - | Fogtech | x | 100% | 50% | 100% | 0% | 0% | 0% | x | x | x | Pressure test completed and Panel side CX l2 checks pending due to non readiness and till =date not offered
F.129 | WMS- T6T7-DG -CATCHER-M2 | ROK | Fire | DG Stack Area | Water Mist System | - | Fogtech | x | 100% | 50% | 100% | 0% | 0% | 0% | x | x | x | Pressure test completed and Panel side CX l2 checks pending due to non readiness and till =date not offered
F.130 | WMS- T6T7-DG -RISER-2 | ROK | Fire | DG Stack Area | Water Mist System | - | Fogtech | x | 100% | 50% | 100% | 0% | 0% | 0% | x | x | x | Pressure test completed and Panel side CX l2 checks pending due to non readiness and till =date not offered
F.131 | WMS- T6T7-DG-CH-2 | ROK | Fire | DG Stack Area | Water Mist System | - | Fogtech | x | 100% | 50% | 100% | 0% | 0% | 0% | x | x | x | Pressure test completed and Panel side CX l2 checks pending due to non readiness and till =date not offered
F.132 | WMS- T6T7-DG-CH-9 | ROK | Fire | DG Stack Area | Water Mist System | - | Fogtech | x | 100% | 50% | 100% | 100% | 0% | 0% | x | x | x | Pressure test completed and Panel side CX l2 checks pending due to non readiness and till =date not offered
F.133 | WMS- T6T7-DG-CH-5 | ROK | Fire | DG Stack Area | Water Mist System | - | Fogtech | x | 100% | 50% | 100% | 100% | 0% | 0% | x | x | x
F.134 | WMS- T6T7-DG-CH-6 | ROK | Fire | DG Stack Area | Water Mist System | - | Fogtech | x | 100% | 50% | 100% | 0% | 0% | 0% | x | x | x
F.135 | WMS- T6T7-DG-RISER-3 | ROK | Fire | DG Stack Area | Water Mist System | - | Fogtech | x | 100% | 50% | 100% | 50% | 0% | 0% | x | x | x | Pressure test completed and Panel side CX l2 checks pending due to non readiness and till =date not offered
F.136 | WMS- T6T7-DG-RISER-4 | ROK | Fire | DG Stack Area | Water Mist System | - | Fogtech | x | 100% | 50% | 100% | 100% | 0% | 0% | x | x | x
F.137 | WMS- T6T7-DG-RISER-1 | ROK | Fire | DG Stack Area | Water Mist System | - | Fogtech | x | 100% | 50% | 100% | 0% | 0% | 0% | x | x | x | Pressure test completed and Panel side CX l2 checks pending due to non readiness and till =date not offered
E.255 | FUEL-Pump-01 | FOK | HSD | HSD Yard | Fuel Transfer Pump | 333 LPM | GMMCO | 100% | 60% | 0% | 0% | 0% | 0% | 0% | x | x | x | supports issue, shaft direction checks are pending, Layout is pending
E.256 | FUEL-Pump-02 | ROK | HSD | HSD Yard | Fuel Transfer Pump | 333 LPM | GMMCO | 100% | 60% | 0% | 0% | 0% | 0% | 0% | x | x | x | supports issue, shaft direction checks are pending, Layout is pending
E.257 | FUEL-Pump-03 | ROK | HSD | HSD Yard | Fuel Transfer Pump | 333 LPM | GMMCO | 100% | 60% | 0% | 0% | 0% | 0% | 0% | x | x | x | supports issue, shaft direction checks are pending, Layout is pending
E.258 | FUEL-Pump-04 | ROK | HSD | HSD Yard | Fuel Transfer Pump | 333 LPM | GMMCO | 100% | 60% | 0% | 0% | 0% | 0% | 0% | x | x | x | supports issue, shaft direction checks are pending, Layout is pending
E.259 | FUEL-Pump-05 | ROK | HSD | HSD Yard | Fuel Transfer Pump | 333 LPM | GMMCO | 100% | 60% | 0% | 0% | 0% | 0% | 0% | x | x | x | supports issue, shaft direction checks are pending, Layout is pending
E.260 | FUEL-Pump-06 | ROK | HSD | HSD Yard | Fuel Transfer Pump | 333 LPM | GMMCO | 100% | 60% | 0% | 0% | 0% | 0% | 0% | x | x | x | supports issue, shaft direction checks are pending, Layout is pending
E.261 | ULD-PUMP-01 | FOK | HSD | HSD Yard | Fuel Unloading Pump | 333 LPM | GMMCO | 100% | 60% | 0% | 0% | 0% | 0% | 0% | x | x | x | supports issue, shaft direction checks are pending, Layout is pending
E.262 | ULD-PUMP-02 | ROK | HSD | HSD Yard | Fuel Unloading Pump | 333 LPM | GMMCO | 100% | 0% | 0% | 0% | 0% | 0% | 0% | x | x | x
E.263 | RTN-PMP-01 | FOK | HSD | DG Stack | Return Tank Pump/Over | 125 LPM | GMMCO | 100% | 0% | 0% | 0% | 0% | 0% | 0% | x | x | x | North-East
E.264 | RTN-PMP-02 | ROK | HSD | DG Stack | Return Tank Pump/Over | 125 LPM | GMMCO | 100% | 0% | 0% | 0% | 0% | 0% | 0% | x | x | x | North-East
E.265 | RTN-PMP-01 | ROK | HSD | DG Stack | Return Tank Pump/Over | 125 LPM | GMMCO | 100% | 0% | 0% | 0% | 0% | 0% | 0% | x | x | x | South-East
E.266 | RTN-PMP-02 | ROK | HSD | DG Stack | Return Tank Pump/Over | 125 LPM | GMMCO | 100% | 0% | 0% | 0% | 0% | 0% | 0% | x | x | x | South-East
E.267 | RTN-PMP-01 | ROK | HSD | DG Stack | Return Tank Pump/Over | 125 LPM | GMMCO | 100% | 0% | 0% | 0% | 0% | 0% | 0% | x | x | x | North-West
E.268 | RTN-PMP-02 | ROK | HSD | DG Stack | Return Tank Pump/Over | 125 LPM | GMMCO | 100% | 0% | 0% | 0% | 0% | 0% | 0% | x | x | x | North-West
E.269 | RTN-PMP-01 | ROK | HSD | DG Stack | Return Tank Pump/Over | 125 LPM | GMMCO | 100% | 0% | 0% | 0% | 0% | 0% | 0% | x | x | x | South-West
E.270 | RTN-PMP-02 | ROK | HSD | DG Stack | Return Tank Pump/Over | 125 LPM | GMMCO | 100% | 0% | 0% | 0% | 0% | 0% | 0% | x | x | x | South-West
E.271 | UGT-01 | ROK | HSD | HSD Yard | Under Ground Tank | 90 KL | GMMCO | 100% | 60% | 0% | 0% | x | x | x | x | x | x | Level transmitter not installed, Updated layout not provided
E.272 | UGT-02 | ROK | HSD | HSD Yard | Under Ground Tank | 90 KL | GMMCO | 100% | 60% | 0% | 0% | x | x | x | x | x | x | Level transmitter not installed, Updated layout not provided
E.273 | UGT-03 | ROK | HSD | HSD Yard | Under Ground Tank | 90 KL | GMMCO | 100% | 60% | 0% | 0% | x | x | x | x | x | x | Level transmitter not installed, Updated layout not provided
E.274 | UGT-04 | ROK | HSD | HSD Yard | Under Ground Tank | 90 KL | GMMCO | 100% | 60% | 0% | 0% | x | x | x | x | x | x | Level transmitter not installed, Updated layout not provided
E.275 | UGT-05 | ROK | HSD | HSD Yard | Under Ground Tank | 90 KL | GMMCO | 100% | 60% | 0% | 0% | x | x | x | x | x | x | Level transmitter not installed, Updated layout not provided
E.276 | UGT-06 | ROK | HSD | HSD Yard | Under Ground Tank | 90 KL | GMMCO | 100% | 60% | 0% | 0% | x | x | x | x | x | x | Level transmitter not installed, Updated layout not provided
E.277 | UGT-07 | ROK | HSD | HSD Yard | Under Ground Tank | 90 KL | GMMCO | 100% | 60% | 0% | 0% | x | x | x | x | x | x | Level transmitter not installed, Updated layout not provided
E.278 | UGT-08 | ROK | HSD | HSD Yard | Under Ground Tank | 90 KL | GMMCO | 100% | 60% | 0% | 0% | x | x | x | x | x | x | Level transmitter not installed, Updated layout not provided
E.279 | UGT-09 | ROK | HSD | HSD Yard | Under Ground Tank | 90 KL | GMMCO | 100% | 60% | 0% | 0% | x | x | x | x | x | x | Level transmitter not installed, Updated layout not provided
E.280 | UGT-10 | ROK | HSD | HSD Yard | Under Ground Tank | 90 KL | GMMCO | 100% | 60% | 0% | 0% | x | x | x | x | x | x | Level transmitter not installed, Updated layout not provided
M.243 | HSD SOO | ROK | HSD | - | HSD SOO | - | - | x | x | x | x | x | x | x | 0% | 0% | 0%
M.001 | Pump ATS- 01 | ROK | Mechanical | Terrace | ATS | 415V | Shinryo Suvidha | x | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | BMS Verification Pending
M.002 | Pump ATS- 02 | ROK | Mechanical | Terrace | ATS | 415V | Shinryo Suvidha | x | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | BMS Verification Pending
M.003 | Pump ATS- 03 | ROK | Mechanical | Terrace | ATS | 415V | Shinryo Suvidha | x | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | BMS Verification Pending
M.004 | Pump ATS- 04 | ROK | Mechanical | Terrace | ATS | 415V | Shinryo Suvidha | x | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | BMS Verification Pending
M.005 | Pump ATS- 05 | ROK | Mechanical | Terrace | ATS | 415V | Shinryo Suvidha | x | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | BMS Verification Pending
M.006 | Pump ATS- 06 | FOK | Mechanical | Terrace | ATS | 415V | Shinryo Suvidha | x | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | BMS Verification Pending
M.007 | FWU-L7-SH-01 | FOK | Mechanical | 7F(L7) | FWU | 144 TR | Vertiv | 100% | 100% | 100% | 100% | 90% | 0% | 0% | 0% | 0% | 0% | BMS verificaiton not done due to BMS not ready . Openings need to be closed, (for air flow verification) Flow verification pending SPP verification pending on availability of second source DP sensor calibration- NA Common for all the units
M.008 | FWU-L7-SH-02 | ROK | Mechanical | 7F(L7) | FWU | 144 TR | Vertiv | 100% | 100% | 100% | 100% | 90% | 0% | 0% | 0% | 0% | 0% | BMS verificaiton not done due to BMS not ready . Openings need to be closed Secondary source need to be made availble Flow verification pending
M.009 | FWU-L7-SH-03 | ROK | Mechanical | 7F(L7) | FWU | 144 TR | Vertiv | 100% | 100% | 100% | 100% | 90% | 0% | 0% | 0% | 0% | 0% | BMS verificaiton not done due to BMS not ready . Openings need to be closed Secondary source need to be made availble Flow verification pending
M.010 | FWU-L7-SH-04 | ROK | Mechanical | 7F(L7) | FWU | 144 TR | Vertiv | 100% | 100% | 100% | 100% | 90% | 0% | 0% | 0% | 0% | 0% | BMS verificaiton not done due to BMS not ready . Openings need to be closed Secondary source need to be made availble Flow verification pending
M.011 | FWU-L7-SH-05 | ROK | Mechanical | 7F(L7) | FWU | 144 TR | Vertiv | 100% | 100% | 100% | 100% | 90% | 0% | 0% | 0% | 0% | 0% | BMS verificaiton not done due to BMS not ready . Openings need to be closed Secondary source need to be made availble Flow verification pending
M.012 | FWU-L7-SH-06 | ROK | Mechanical | 7F(L7) | FWU | 144 TR | Vertiv | 100% | 100% | 100% | 100% | 90% | 0% | 0% | 0% | 0% | 0% | BMS verificaiton not done due to BMS not ready . Openings need to be closed Secondary source need to be made availble Flow verification pending
M.013 | FWU-L7-SH-07 | ROK | Mechanical | 7F(L7) | FWU | 144 TR | Vertiv | 100% | 100% | 100% | 100% | 90% | 0% | 0% | 0% | 0% | 0%
M.014 | FWU-L7-SH-08 | ROK | Mechanical | 7F(L7) | FWU | 144 TR | Vertiv | 100% | 100% | 100% | 100% | 90% | 0% | 0% | 0% | 0% | 0%
M.015 | FWU-L7-SH-09 | ROK | Mechanical | 7F(L7) | FWU | 144 TR | Vertiv | 100% | 100% | 100% | 100% | 90% | 0% | 0% | 0% | 0% | 0%
M.016 | FWU-L7-SH-10 | ROK | Mechanical | 7F(L7) | FWU | 144 TR | Vertiv | 100% | 100% | 100% | 100% | 90% | 0% | 0% | 0% | 0% | 0%
M.017 | FWU-L7-SH-11 | ROK | Mechanical | 7F(L7) | FWU | 144 TR | Vertiv | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0%
M.018 | FWU-L7-SH-12 | ROK | Mechanical | 7F(L7) | FWU | 144 TR | Vertiv | 100% | 100% | 100% | 100% | 90% | 0% | 0% | 0% | 0% | 0%
M.019 | FWU-L7-SH-13 | ROK | Mechanical | 7F(L7) | FWU | 144 TR | Vertiv | 100% | 100% | 100% | 100% | 90% | 0% | 0% | 0% | 0% | 0%
M.020 | FWU-L7-SH-14 | ROK | Mechanical | 7F(L7) | FWU | 144 TR | Vertiv | 100% | 100% | 100% | 100% | 90% | 0% | 0% | 0% | 0% | 0%
M.021 | FWU-L7-SH-15 | ROK | Mechanical | 7F(L7) | FWU | 144 TR | Vertiv | 100% | 100% | 100% | 100% | 90% | 0% | 0% | 0% | 0% | 0%
M.022 | FWU-L7-SH-16 | ROK | Mechanical | 7F(L7) | FWU | 144 TR | Vertiv | 100% | 100% | 100% | 100% | 90% | 0% | 0% | 0% | 0% | 0%
M.023 | FWU-L7-SH-17 | ROK | Mechanical | 7F(L7) | FWU | 144 TR | Vertiv | 100% | 100% | 100% | 100% | 90% | 0% | 0% | 0% | 0% | 0%
M.024 | FWU-L7-SH-18 | ROK | Mechanical | 7F(L7) | FWU | 144 TR | Vertiv | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0%
M.025 | FWU-L7-SH-19 | ROK | Mechanical | 7F(L7) | FWU | 144 TR | Vertiv | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0%
M.026 | FWU-L7-SH-20 | ROK | Mechanical | 7F(L7) | FWU | 144 TR | Vertiv | 100% | 100% | 100% | 100% | 90% | 0% | 0% | 0% | 0% | 0%
M.027 | CDU-L7-SH-01 | FOK | Mechanical | 7F(L7) | CDU | 364 TR | Schneider LC | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Unit name tag, with serial no is needed to upload the reports
M.028 | CDU-L7-SH-02 | ROK | Mechanical | 7F(L7) | CDU | 364 TR | Schneider LC | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Unit name tag, with serial no is needed to upload the reports
M.029 | CDU-L7-SH-03 | ROK | Mechanical | 7F(L7) | CDU | 364 TR | Schneider LC | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Unit name tag, with serial no is needed to upload the reports
M.030 | CDU-L7-SH-04 | ROK | Mechanical | 7F(L7) | CDU | 364 TR | Schneider LC | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Unit name tag, with serial no is needed to upload the reports
M.031 | CDU-L7-SH-05 | ROK | Mechanical | 7F(L7) | CDU | 364 TR | Schneider LC | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Unit name tag, with serial no is needed to upload the reports
M.032 | SFN | ROK | Mechanical | 7F(L7) | SFN | - | Schneider LC | 100% | 0% | 0% | 0% | X | X | X | x | x | x
M.033 | PAHU-T6-L7-A2-BATT-RM1 | ROK | Mechanical | 7F(L7) | PAHU | 2 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99% | 100% | Updatated screenshot recvied 31-08-2026 - SS report in progress CxL4 SS shared on 31-08-2026
M.034 | PAHU-T6-L7-A2-BATT-RM2 | ROK | Mechanical | 7F(L7) | PAHU | 2 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99% | 100% | Updatated screenshot recvied 31-08-2026 - SS report in progress CxL4 SS shared on 31-08-2026
M.035 | PAHU-T6-L7-A2-ELECT-UPS-RM1 | ROK | Mechanical | 7F(L7) | PAHU | 17 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 99% | 100% | 100% | 99% | 100% | Updatated screenshot recvied 31-08-2026 - SS report in progress CxL4 SS shared on 31-08-2026
M.036 | PAHU-T6-L7-A2-ELECT-UPS-RM2 | ROK | Mechanical | 7F(L7) | PAHU | 17 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 99% | 100% | 100% | 99% | 100% | Updatated screenshot recvied 31-08-2026 - SS report in progress CxL4 SS shared on 31-08-2026
M.037 | PAHU-T6-L7-B2-ELECT-UPS-RM1 | ROK | Mechanical | 7F(L7) | PAHU | 10 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 99% | 100% | 100% | 99% | 100% | Updatated screenshot recvied 31-08-2026 - SS report in progress CxL4 SS shared on 31-08-2026
M.038 | PAHU-T6-L7-B2-ELECT-UPS-RM2 | ROK | Mechanical | 7F(L7) | PAHU | 10 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 99% | 100% | 100% | 99% | 100% | Updatated screenshot recvied 31-08-2026 - SS report in progress CxL4 SS shared on 31-08-2026
M.039 | PAHU-T6-L7-B2-BATT-RM1 | ROK | Mechanical | 7F(L7) | PAHU | 2 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99% | 100% | Updatated screenshot recvied 31-08-2026 - SS report in progress CxL4 SS shared on 31-08-2026
M.040 | PAHU-T6-L7-B2-BATT-RM2 | ROK | Mechanical | 7F(L7) | PAHU | 2 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99% | 100% | Updatated screenshot recvied 31-08-2026 - SS report in progress CxL4 SS shared on 31-08-2026
M.041 | PAHU-T7-L7-A2-ELECT-UPS-RM1 | ROK | Mechanical | 7F(L7) | PAHU | 3 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 99% | 100% | 100% | 99% | 100% | Updatated screenshot recvied 31-08-2026 - SS report in progress CxL4 SS shared on 31-08-2026
M.042 | PAHU-T7-L7-A2-ELECT-UPS-RM2 | ROK | Mechanical | 7F(L7) | PAHU | 3 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 99% | 100% | 100% | 99% | 100% | Updatated screenshot recvied 31-08-2026 - SS report in progress CxL4 SS shared on 31-08-2026
M.043 | PAHU-T7-L7-B2-ELECT-UPS-RM1 | ROK | Mechanical | 7F(L7) | PAHU | 3 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 99% | 100% | 100% | 99% | 100% | Updatated screenshot recvied 31-08-2026 - SS report in progress CxL4 SS shared on 31-08-2026
M.044 | PAHU-T7-L7-B2-ELECT-UPS-RM2 | ROK | Mechanical | 7F(L7) | PAHU | 3 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 99% | 100% | 100% | 99% | 100% | Updatated screenshot recvied 31-08-2026 - SS report in progress CxL4 SS shared on 31-08-2026
M.045 | PAHU-L7-MMRYZ-2-1 | ROK | Mechanical | 7F(L7) | PAHU | 26 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 50% | 99% | 0% | Updatated screenshot recvied 31-08-2026 - SS report in progress
M.046 | PAHU-L7-MMRYZ-2-2 | ROK | Mechanical | 7F(L7) | PAHU | 26 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 50% | 99% | 0% | Updatated screenshot recvied 31-08-2026 - SS report in progress
M.047 | PAHU-L7-MMRYZ-2-3 | FOK | Mechanical | 7F(L7) | PAHU | 26 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 50% | 99% | 0% | Updatated screenshot recvied 31-08-2026 - SS report in progress
M.048 | PAHU-L7-MMRYZ-2-4 | ROK | Mechanical | 7F(L7) | PAHU | 26 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 50% | 99% | 0% | Updatated screenshot recvied 31-08-2026 - SS report in progress
M.049 | PAHU-T7-L7-B1-ELECT-UPS-RM1 | ROK | Mechanical | 7F(L7) | PAHU | 3 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 99% | 100% | 100% | 99% | 100% | Updatated screenshot recvied 31-08-2026 - SS report in progress CxL4 SS shared on 31-08-2026
M.050 | PAHU-T7-L7-B1-ELECT-UPS-RM2 | ROK | Mechanical | 7F(L7) | PAHU | 3 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 99% | 100% | 100% | 99% | 100% | Updatated screenshot recvied 31-08-2026 - SS report in progress CxL4 SS shared on 31-08-2026
M.051 | PAHU-T7-L7-A1-ELECT-UPS-RM1 | ROK | Mechanical | 7F(L7) | PAHU | 3 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 99% | 100% | 100% | 99% | 100% | Updatated screenshot recvied 31-08-2026 - SS report in progress CxL4 SS shared on 31-08-2026
M.052 | PAHU-T7-L7-A1-ELECT-UPS-RM2 | ROK | Mechanical | 7F(L7) | PAHU | 3 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 99% | 100% | 100% | 99% | 100% | Updatated screenshot recvied 31-08-2026 - SS report in progress CxL4 SS shared on 31-08-2026
M.053 | PAHU-T6-L7-B1-BATT-RM1 | ROK | Mechanical | 7F(L7) | PAHU | 2 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99% | 100% | Updatated screenshot recvied 31-08-2026 - SS report in progress CxL4 SS shared on 31-08-2026
M.054 | PAHU-T6-L7-B1-BATT-RM2 | ROK | Mechanical | 7F(L7) | PAHU | 2 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99% | 100% | Updatated screenshot recvied 31-08-2026 - SS report in progress CxL4 SS shared on 31-08-2026
M.055 | PAHU-T6-L7-B1-ELECT-UPS-RM1 | ROK | Mechanical | 7F(L7) | PAHU | 10 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 99% | 100% | 100% | 99% | 100% | Updatated screenshot recvied 31-08-2026 - SS report in progress CxL4 SS shared on 31-08-2026
M.056 | PAHU-T6-L7-B1-ELECT-UPS-RM2 | ROK | Mechanical | 7F(L7) | PAHU | 10 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 99% | 100% | 100% | 99% | 100% | Updatated screenshot recvied 31-08-2026 - SS report in progress CxL4 SS shared on 31-08-2026
M.057 | PAHU-T6-L7-A1-ELECT-UPS-RM1 | ROK | Mechanical | 7F(L7) | PAHU | 17 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 99% | 100% | 100% | 99% | 100% | Updatated screenshot recvied 31-08-2026 - SS report in progress CxL4 SS shared on 31-08-2026
M.058 | PAHU-T6-L7-A1-ELECT-UPS-RM2 | ROK | Mechanical | 7F(L7) | PAHU | 17 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 99% | 100% | 100% | 99% | 100% | Updatated screenshot recvied 31-08-2026 - SS report in progress CxL4 SS shared on 31-08-2026
M.059 | PAHU-T6-L7-A1-BATT-RM1 | ROK | Mechanical | 7F(L7) | PAHU | 2 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99% | 100% | Updatated screenshot recvied 31-08-2026 - SS report in progress CxL4 SS shared on 31-08-2026
M.060 | PAHU-T6-L7-A1-BATT-RM2 | ROK | Mechanical | 7F(L7) | PAHU | 2 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99% | 100% | Updatated screenshot recvied 31-08-2026 - SS report in progress CxL4 SS shared on 31-08-2026
M.061 | PAHU-L7-MMRYZ-1-1 | ROK | Mechanical | 7F(L7) | PAHU | 26 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 50% | 0% | 0% | Updatated screenshot recvied 31-08-2026 - SS report in progress
M.062 | PAHU-L7-MMRYZ-1-2 | ROK | Mechanical | 7F(L7) | PAHU | 26 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 50% | 0% | 0% | Updatated screenshot recvied 31-08-2026 - SS report in progress
M.063 | PAHU-L7-MMRYZ-1-3 | ROK | Mechanical | 7F(L7) | PAHU | 26 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 50% | 0% | 0% | Updatated screenshot recvied 31-08-2026 - SS report in progress
M.064 | PAHU-L7-MMRYZ-1-4 | ROK | Mechanical | 7F(L7) | PAHU | 26 TR | STULZ | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 50% | 0% | 0% | Updatated screenshot recvied 31-08-2026 - SS report in progress
M.065 | TFA-L7-A1 | FOK | Mechanical | 7F(L7) | TFA | 1500 CFM | CDVL | x | 100% | 100% | 100% | 100% | 99% | 100% | x | x | x | BMS SS report is pending, Caliration ceritifcate pending
M.066 | TFA-L7-B1 | ROK | Mechanical | 7F(L7) | TFA | 1500 CFM | CDVL | x | 100% | 100% | 100% | 100% | 99% | 100% | x | x | x | BMS SS report is pending, Caliration ceritifcate pending
M.067 | TFA-L7-A2 | ROK | Mechanical | 7F(L7) | TFA | 1500 CFM | CDVL | x | 100% | 100% | 100% | 100% | 99% | 100% | x | x | x | BMS SS report is pending, Caliration ceritifcate pending
M.068 | TFA-L7-B2 | ROK | Mechanical | 7F(L7) | TFA | 1500 CFM | CDVL | x | 100% | 100% | 100% | 100% | 99% | 100% | x | x | x | BMS SS report is pending, Caliration ceritifcate pending
M.069 | TFA-T6-GF-1 | FOK | Mechanical | GF(L0) | TFA | 1500 CFM | Safe Air | x | 100% | 99% | 100% | 0% | 0% | 0% | x | x | x | Pressure test report pending, vacuming reports, duct smoke test
M.070 | TFA-T7-GF-1 | ROK | Mechanical | GF(L0) | TFA | 1500 CFM | Safe Air | x | 100% | 99% | 100% | 0% | 0% | 0% | x | x | x | Pressure test report pending, vacuming reports, duct smoke test
M.071 | ODU-L7-TFA-A1 | ROK | Mechanical | 7F(L7) | ODU | 12 HP | CDVL | x | 100% | 100% | 100% | 100% | 99% | 100% | x | x | x
M.072 | ODU-L7-TFA-A2 | ROK | Mechanical | 7F(L7) | ODU | 12 HP | CDVL | x | 100% | 90% | 100% | 100% | 99% | 100% | x | x | x | In the Pressure test report - Initial date and final date (10 days Gap) - ODU updated TDS not share by Vendor, Incorrect Calibration certificate shared
M.073 | ODU-L7-TFA-B1 | ROK | Mechanical | 7F(L7) | ODU | 12 HP | CDVL | x | 100% | 100% | 100% | 100% | 99% | 100% | x | x | x
M.074 | ODU-L7-TFA-B2 | ROK | Mechanical | 7F(L7) | ODU | 12 HP | CDVL | x | 100% | 90% | 100% | 100% | 99% | 100% | x | x | x | In the Pressure test report - Initial date and final date (10 days Gap) - ODU updated TDS not share by Vendor, Incorrect Calibration certificate shared
M.075 | ODU-TFA-T6-GF-1 | ROK | Mechanical | GF(L0) | ODU | 12 HP | Safe Air | x | 100% | 99% | 100% | 0% | 0% | 0% | x | x | x | Pressure test report pending, vacuming reports, duct smoke test
M.076 | ODU-TFA-T7-GF-1 | ROK | Mechanical | GF(L0) | ODU | 12 HP | Safe Air | x | 100% | 99% | 100% | 0% | 0% | 0% | x | x | x | Pressure test report pending, vacuming reports, duct smoke test
M.077 | FCU-L7-COR-1 | ROK | Mechanical | 7F(L7) | FCU | 2 TR | CDVL | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Report preparation inprogress, submited by 11-08-2026 by Pradeep
M.078 | FCU-L7-COR-2 | ROK | Mechanical | 7F(L7) | FCU | 2 TR | CDVL | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Report preparation inprogress, submited by 11-08-2026 by Pradeep
M.079 | FCU-L7-COR-3 | ROK | Mechanical | 7F(L7) | FCU | 2 TR | CDVL | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Report preparation inprogress, submited by 11-08-2026 by Pradeep
M.080 | FCU-L7-COR-4 | ROK | Mechanical | 7F(L7) | FCU | 2 TR | CDVL | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Report preparation inprogress, submited by 11-08-2026 by Pradeep
M.081 | FCU-L7-COR-5 | ROK | Mechanical | 7F(L7) | FCU | 2 TR | CDVL | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Report preparation inprogress, submited by 11-08-2026 by Pradeep
M.082 | FCU-L7-COR-6 | ROK | Mechanical | 7F(L7) | FCU | 2 TR | CDVL | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Report preparation inprogress, submited by 11-08-2026 by Pradeep
M.083 | FCU-L7-COR-7 | ROK | Mechanical | 7F(L7) | FCU | 2 TR | CDVL | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Report preparation inprogress, submited by 11-08-2026 by Pradeep
M.084 | FCU-L7-COR-8 | ROK | Mechanical | 7F(L7) | FCU | 2 TR | CDVL | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Report preparation inprogress, submited by 11-08-2026 by Pradeep
M.085 | FCU-L7-COR-9 | ROK | Mechanical | 7F(L7) | FCU | 2 TR | CDVL | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Report preparation inprogress, submited by 11-08-2026 by Pradeep
M.086 | FCU-L7-COR-10 | ROK | Mechanical | 7F(L7) | FCU | 2 TR | CDVL | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Report preparation inprogress, submited by 11-08-2026 by Pradeep
M.087 | FCU-L7-COR-11 | ROK | Mechanical | 7F(L7) | FCU | 2 TR | CDVL | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Report preparation inprogress, submited by 11-08-2026 by Pradeep
M.088 | FCU-L7-ST-RM-1 | ROK | Mechanical | 7F(L7) | FCU | 2 TR | CDVL | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Report preparation inprogress, submited by 11-08-2026 by Pradeep
M.089 | FCU-L7-STR-2 | ROK | Mechanical | 7F(L7) | FCU | 2 TR | CDVL | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Report preparation inprogress, submited by 11-08-2026 by Pradeep
M.090 | FCU-L7-STR-RM-3 | ROK | Mechanical | 7F(L7) | FCU | 2 TR | CDVL | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Report preparation inprogress, submited by 11-08-2026 by Pradeep
M.091 | FCU-L7-STR-4 | ROK | Mechanical | 7F(L7) | FCU | 2 TR | CDVL | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Report preparation inprogress, submited by 11-08-2026 by Pradeep
M.092 | FCU-L7-STR-5 | ROK | Mechanical | 7F(L7) | FCU | 2 TR | CDVL | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Report preparation inprogress, submited by 11-08-2026 by Pradeep
M.093 | FCU-L7-STR-RM-6 | ROK | Mechanical | 7F(L7) | FCU | 2 TR | CDVL | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Report preparation inprogress, submited by 11-08-2026 by Pradeep
M.094 | FCU-L7-ST-RM-7 | ROK | Mechanical | 7F(L7) | FCU | 2 TR | CDVL | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Report preparation inprogress, submited by 11-08-2026 by Pradeep
M.095 | FCU-L7-STR-8 | ROK | Mechanical | 7F(L7) | FCU | 2 TR | CDVL | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Report preparation inprogress, submited by 11-08-2026 by Pradeep
M.096 | FCU-L7-MG-1 | ROK | Mechanical | 7F(L7) | FCU | 2 TR | CDVL | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Report preparation inprogress, submited by 11-08-2026 by Pradeep
M.097 | FCU-L7-MG-2 | ROK | Mechanical | 7F(L7) | FCU | 2 TR | CDVL | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Report preparation inprogress, submited by 11-08-2026 by Pradeep
M.098 | FCU-L7-MG-3 | ROK | Mechanical | 7F(L7) | FCU | 2 TR | CDVL | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Report preparation inprogress, submited by 11-08-2026 by Pradeep
M.099 | FCU-L7-MG-4 | ROK | Mechanical | 7F(L7) | FCU | 2 TR | CDVL | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Report preparation inprogress, submited by 11-08-2026 by Pradeep
M.100 | FCU-L7-MD-1 | ROK | Mechanical | 7F(L7) | FCU | 2 TR | CDVL | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Report preparation inprogress, submited by 11-08-2026 by Pradeep
M.101 | FCU-L7-MD-2 | ROK | Mechanical | 7F(L7) | FCU | 2 TR | CDVL | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Report preparation inprogress, submited by 11-08-2026 by Pradeep
M.102 | FCU-L7-SPARE BBU SRM | ROK | Mechanical | 7F(L7) | FCU | 2 TR | CDVL | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Report preparation inprogress, submited by 11-08-2026 by Pradeep
M.103 | FCU-L7-Spent BBU SRM | ROK | Mechanical | 7F(L7) | FCU | 2 TR | CDVL | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Report preparation inprogress, submited by 11-08-2026 by Pradeep
M.104 | FCU-L7-DCO | ROK | Mechanical | 7F(L7) | FCU | 2 TR | CDVL | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Report preparation inprogress, submited by 11-08-2026 by Pradeep
M.105 | FCU-L7-SCM | ROK | Mechanical | 7F(L7) | FCU | 2 TR | CDVL | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Report preparation inprogress, submited by 11-08-2026 by Pradeep
M.106 | FCU-L7-NBBS-1 | ROK | Mechanical | 7F(L7) | FCU | 3 TR | CDVL | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Report preparation inprogress, submited by 11-08-2026 by Pradeep
M.107 | FCU-L7-NBB-2 | ROK | Mechanical | 7F(L7) | FCU | 3 TR | CDVL | x | 100% | 100% | 100% | 100% | 100% | 100% | x | x | x | Report preparation inprogress, submited by 11-08-2026 by Pradeep
M.108 | EX-L7-01 | FOK | Mechanical | 7F(L7) | Smoke Exhaust Fan | 1200 CFM | CDVL | x | 100% | 100% | 100% | 90% | 0% | 0% | x | x | x | Motor rated current value is not available in the TDS that should confirm OEM, BMS verificaiton is pending
M.109 | EX-L7-02 | ROK | Mechanical | 7F(L7) | Smoke Exhaust Fan | 1200 CFM | CDVL | x | 100% | 100% | 100% | 90% | 0% | 0% | x | x | x | Motor rated current value is not available in the TDS that should confirm OEM, BMS verificaiton is pending
M.110 | EX-L7-03 | ROK | Mechanical | 7F(L7) | Smoke Exhaust Fan | 1200 CFM | CDVL | x | 100% | 100% | 100% | 90% | 0% | 0% | x | x | x | Motor rated current value is not available in the TDS that should confirm OEM, BMS verificaiton is pending
M.111 | EX-L7-04 | ROK | Mechanical | 7F(L7) | Smoke Exhaust Fan | 1200 CFM | CDVL | x | 100% | 100% | 100% | 90% | 0% | 0% | x | x | x | BMS verificaiton is pending
M.112 | EX-L7-05 | ROK | Mechanical | 7F(L7) | Smoke Exhaust Fan | 1200 CFM | CDVL | x | 100% | 100% | 100% | 90% | 0% | 0% | x | x | x | BMS verificaiton is pending
M.113 | EX-L7-06 | ROK | Mechanical | 7F(L7) | Smoke Exhaust Fan | 1200 CFM | CDVL | x | 100% | 100% | 100% | 90% | 0% | 0% | x | x | x | BMS verificaiton is pending
M.114 | EF-T6-TRN-1-L0-1 | FOK | Mechanical | GF(L0) | Smoke Exhaust Fan | 1200 CFM | Safe Air | x | 100% | 0% | 100% | 100% | 100% | 100% | x | x | x
M.115 | EF-T6-TRN-2-L0-1 | ROK | Mechanical | GF(L0) | Smoke Exhaust Fan | 1200 CFM | Safe Air | x | 100% | 0% | 100% | 100% | 100% | 100% | x | x | x
M.116 | EF-T6-TRN-3-L0-1 | ROK | Mechanical | GF(L0) | Smoke Exhaust Fan | 1200 CFM | Safe Air | x | 100% | 0% | 100% | 100% | 100% | 100% | x | x | x
M.117 | EF-T6-TRN-4 | ROK | Mechanical | GF(L0) | Smoke Exhaust Fan | 1200 CFM | Safe Air | x | 100% | 99% | 100% | 100% | 100% | 100% | x | x | x
M.118 | EF-T6-TRN-5 | ROK | Mechanical | GF(L0) | Smoke Exhaust Fan | 1200 CFM | Safe Air | x | 100% | 99% | 100% | 100% | 100% | 100% | x | x | x
M.119 | EF-T6-TRN-6 | ROK | Mechanical | GF(L0) | Smoke Exhaust Fan | 1200 CFM | Safe Air | x | 100% | 99% | 100% | 100% | 100% | 100% | x | x | x
M.120 | EF-T6-TRN-7 | ROK | Mechanical | GF(L0) | Smoke Exhaust Fan | 1200 CFM | Safe Air | x | 100% | 99% | 100% | 100% | 100% | 100% | x | x | x
M.121 | EF-T6-TRN-8 | ROK | Mechanical | GF(L0) | Smoke Exhaust Fan | 1200 CFM | Safe Air | x | 100% | 99% | 100% | 100% | 100% | 100% | x | x | x
M.122 | EF-T6-TRN-9 | ROK | Mechanical | GF(L0) | Smoke Exhaust Fan | 1200 CFM | Safe Air | x | 100% | 99% | 100% | 100% | 100% | 100% | x | x | x
M.123 | EF-T6-TRN-10 | ROK | Mechanical | GF(L0) | Smoke Exhaust Fan | 1200 CFM | Safe Air | x | 100% | 99% | 100% | 100% | 100% | 100% | x | x | x
M.124 | EF-T6-TRN-11 | ROK | Mechanical | GF(L0) | Smoke Exhaust Fan | 1200 CFM | Safe Air | x | 100% | 99% | 100% | 60% | 100% | 0% | x | x | x | Damper issue
M.125 | EF-T6-TRN-12 | ROK | Mechanical | GF(L0) | Smoke Exhaust Fan | 1200 CFM | Safe Air | x | 100% | 99% | 100% | 100% | 100% | 100% | x | x | x
M.126 | EF-T6-TRN-13 | ROK | Mechanical | GF(L0) | Smoke Exhaust Fan | 1200 CFM | Safe Air | x | 100% | 99% | 100% | 100% | 100% | 0% | x | x | x
M.127 | EF-T6-TRN-14 | ROK | Mechanical | GF(L0) | Smoke Exhaust Fan | 1200 CFM | Safe Air | x | 100% | 99% | 100% | 100% | 100% | 0% | x | x | x
M.128 | EF-T6-HT-1 | ROK | Mechanical | GF(L0) | Smoke Exhaust Fan | 1200 CFM | Safe Air | x | 100% | 99% | 100% | 60% | 100% | 0% | x | x | x | Contactor Trip switch
M.129 | EF-T6-HT-2 | ROK | Mechanical | GF(L0) | Smoke Exhaust Fan | 1200 CFM | Safe Air | x | 100% | 99% | 100% | 100% | 100% | 0% | x | x | x
M.130 | EF-T7-TRN-1 | ROK | Mechanical | GF(L0) | Smoke Exhaust Fan | 1200 CFM | Safe Air | x | 100% | 99% | 100% | 100% | 100% | 100% | x | x | x
M.131 | EF-T7-TRN-2 | ROK | Mechanical | GF(L0) | Smoke Exhaust Fan | 1200 CFM | Safe Air | x | 90% | 80% | 100% | 100% | 100% | 100% | x | x | x
M.132 | EF-T7-TRN-3 | ROK | Mechanical | GF(L0) | Smoke Exhaust Fan | 1200 CFM | Safe Air | x | 90% | 80% | 100% | 100% | 100% | 100% | x | x | x
M.133 | EF-T7-TRN-4 | ROK | Mechanical | GF(L0) | Smoke Exhaust Fan | 1200 CFM | Safe Air | x | 100% | 99% | 100% | 100% | 100% | 100% | x | x | x
M.134 | EF-T7-TRN-5 | ROK | Mechanical | GF(L0) | Smoke Exhaust Fan | 1200 CFM | Safe Air | x | 100% | 99% | 100% | 100% | 100% | 100% | x | x | x
M.135 | EF-T7-TRN-6 | ROK | Mechanical | GF(L0) | Smoke Exhaust Fan | 1200 CFM | Safe Air | x | 100% | 99% | 100% | 100% | 100% | 100% | x | x | x
M.136 | EF-T7-TRN-7 | ROK | Mechanical | GF(L0) | Smoke Exhaust Fan | 1200 CFM | Safe Air | x | 100% | 99% | 100% | 100% | 100% | 100% | x | x | x
M.137 | EF-T7-TRN-8 | ROK | Mechanical | GF(L0) | Smoke Exhaust Fan | 1200 CFM | Safe Air | x | 100% | 99% | 100% | 100% | 100% | 100% | x | x | x
M.138 | EF-T7-TRN-9 | ROK | Mechanical | GF(L0) | Smoke Exhaust Fan | 1200 CFM | Safe Air | x | 100% | 99% | 100% | 100% | 100% | 100% | x | x | x
M.139 | EF-T7-TRN-10 | ROK | Mechanical | GF(L0) | Smoke Exhaust Fan | 1200 CFM | Safe Air | x | 100% | 99% | 100% | 100% | 100% | 100% | x | x | x
M.140 | EF-T7-TRN-11 | ROK | Mechanical | GF(L0) | Smoke Exhaust Fan | 1200 CFM | Safe Air | x | 100% | 99% | 100% | 100% | 100% | 100% | x | x | x
M.141 | EF-T7-TRN-12 | ROK | Mechanical | GF(L0) | Smoke Exhaust Fan | 1200 CFM | Safe Air | x | 100% | 99% | 100% | 100% | 100% | 100% | x | x | x
M.142 | EF-T7-HT-1 | ROK | Mechanical | GF(L0) | Smoke Exhaust Fan | 1200 CFM | Safe Air | x | 100% | 99% | 100% | 100% | 100% | 100% | x | x | x
M.143 | EF-T7-HT-2 | ROK | Mechanical | GF(L0) | Smoke Exhaust Fan | 1200 CFM | Safe Air | x | 100% | 99% | 100% | 100% | 100% | 100% | x | x | x
M.144 | EF-T7-D-BOX | ROK | Mechanical | GF(L0) | Smoke Exhaust Fan | 1200 CFM | Safe Air | x | 100% | 40% | 100% | 70% | 60% | 0% | x | x | x | BMS status is not shown
M.145 | TF-L7-A1 | FOK | Mechanical | 7F(L7) | Transfer Fan | 300 CFM | CDVL | x | 100% | 100% | 100% | 100% | 0% | 100% | x | x | x | L3 Report Prepation Pending, SS shared by SIFY Pathmesh
M.146 | TF-L7-A2 | ROK | Mechanical | 7F(L7) | Transfer Fan | 300 CFM | CDVL | x | 100% | 100% | 100% | 100% | 0% | 100% | x | x | x | L3 Report Prepation Pending, SS shared by SIFY Pathmesh
M.147 | TF-L7-B1 | ROK | Mechanical | 7F(L7) | Transfer Fan | 300 CFM | CDVL | x | 100% | 100% | 100% | 100% | 0% | 100% | x | x | x | L3 Report Prepation Pending, SS shared by SIFY Pathmesh
M.148 | TF-L7-B2 | ROK | Mechanical | 7F(L7) | Transfer Fan | 300 CFM | CDVL | x | 100% | 100% | 100% | 100% | 0% | 100% | x | x | x | L3 Report Prepation Pending, SS shared by SIFY Pathmesh
M.149 | VF-L7-01 | ROK | Mechanical | 7F(L7) | Ventilation Fan | 1100 CFM | CDVL | x | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x
M.150 | VF-L7-02 | ROK | Mechanical | 7F(L7) | Ventilation Fan | 1100 CFM | CDVL | x | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x
M.151 | VF-L7-03 | FOK | Mechanical | 7F(L7) | Ventilation Fan | 350 CFM | CDVL | x | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | Airflow need to mention in as-built for the respective rooms and VCD not installed
M.152 | VF-L7-04 | ROK | Mechanical | 7F(L7) | Ventilation Fan | 350 CFM | CDVL | x | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | Airflow need to mention in as-built for the respective rooms and VCD not installed
M.153 | VF-L7-05 | ROK | Mechanical | 7F(L7) | Ventilation Fan | 800 CFM | CDVL | x | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x
M.154 | VF-L7-06 | ROK | Mechanical | 7F(L7) | Ventilation Fan | 800 CFM | CDVL | x | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x
M.155 | Aux Chiller -01 | ROK | Mechanical | Upper Terrace | Air Cooled Chiller | 364 TR | Sweagon | 100% | 100% | 100% | 100% | 60% | 0% | 0% | 0% | 0% | 0%
M.156 | Aux Chiller -02 | ROK | Mechanical | Upper Terrace | Air Cooled Chiller | 364 TR | Sweagon | 100% | 100% | 100% | 100% | 60% | 0% | 0% | 0% | 0% | 0%
M.157 | Aux Chiller -03 | FOK | Mechanical | Upper Terrace | Air Cooled Chiller | 364 TR | Sweagon | 100% | 100% | 100% | 100% | 60% | 0% | 0% | 0% | 0% | 0% | CPM installtion pending, CHW Pipe connection pending,
M.158 | ACC- 01 | FOK | Mechanical | Upper Terrace | Air Cooled Chiller | 590 TR | Vertiv | 100% | 100% | 100% | 100% | 50% | 0% | 0% | 0% | 0% | 0% | With unit to be submitted
M.159 | ACC- 02 | ROK | Mechanical | Upper Terrace | Air Cooled Chiller | 590 TR | Vertiv | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
M.160 | ACC- 03 | ROK | Mechanical | Upper Terrace | Air Cooled Chiller | 590 TR | Vertiv | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
M.161 | ACC- 04 | ROK | Mechanical | Upper Terrace | Air Cooled Chiller | 590 TR | Vertiv | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
M.162 | ACC- 05 | ROK | Mechanical | Upper Terrace | Air Cooled Chiller | 590 TR | Vertiv | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
M.163 | ACC- 06 | ROK | Mechanical | Upper Terrace | Air Cooled Chiller | 590 TR | Vertiv | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
M.164 | ACC- 07 | ROK | Mechanical | Upper Terrace | Air Cooled Chiller | 590 TR | Vertiv | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
M.165 | ACC- 08 | ROK | Mechanical | Upper Terrace | Air Cooled Chiller | 590 TR | Vertiv | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
M.166 | SCWP-01 | ROK | Mechanical | Upper Terrace | Secondary Chillwater Pump | 1622 GPM | Shinryo Suvidha | 100% | 100% | 100% | 100% | 30% | 0% | 0% | x | x | x
M.167 | SCWP-02 | ROK | Mechanical | Upper Terrace | Secondary Chillwater Pump | 1622 GPM | Shinryo Suvidha | 100% | 100% | 100% | 100% | 30% | 0% | 0% | x | x | x
M.168 | SCWP-03 | ROK | Mechanical | Upper Terrace | Secondary Chillwater Pump | 1622 GPM | Shinryo Suvidha | 100% | 100% | 100% | 100% | 30% | 0% | 0% | x | x | x | Torque Test , Genral stability test & visual inspection checks Pending
M.169 | SCWP-04 | ROK | Mechanical | Upper Terrace | Secondary Chillwater Pump | 1622 GPM | Shinryo Suvidha | 100% | 100% | 100% | 100% | 30% | 0% | 0% | x | x | x | Torque Test , Genral stability test & visual inspection checks Pending
M.170 | SCWP-05 | ROK | Mechanical | Upper Terrace | Secondary Chillwater Pump | 1622 GPM | Shinryo Suvidha | 100% | 100% | 100% | 100% | 30% | 0% | 0% | x | x | x | Torque Test , Genral stability test & visual inspection checks Pending
M.171 | SCWP-06 | FOK | Mechanical | Upper Terrace | Secondary Chillwater Pump | 1622 GPM | Shinryo Suvidha | 99% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | Torque Test , Genral stability test & visual inspection checks Pending - L1 report need to be upload
M.172 | Pressurisation Pump -01 | FOK | Mechanical | Terrace | Pressurisation Pump | 2100 GPM | CDVL | x | 100% | 95% | 0% | 0% | 0% | 0% | x | x | x | TDS and drawing submission pending from vendor side.
M.173 | Pressurisation Pump -02 | ROK | Mechanical | Terrace | Pressurisation Pump | 2100 GPM | CDVL | x | 100% | 95% | 0% | 0% | 0% | 0% | x | x | x | TDS and drawing submission pending from vendor side.
M.174 | Quick Fill Pump-01 | FOK | Mechanical | Terrace | Quick Fill Pump | 2100 GPM | Shinryo Suvidha | 100% | 95% | 90% | 0% | 0% | 0% | 0% | x | x | x | IR Continuty Report and Piping diagram is pending
M.175 | Quick Fill Pump-02 | ROK | Mechanical | Terrace | Quick Fill Pump | 2100 GPM | Shinryo Suvidha | 100% | 95% | 90% | 0% | 50% | 0% | 0% | x | x | x | IR Continuty Report and Piping diagram is pending
M.176 | PAC-T6-L0-TRN1-1 | ROK | Mechanical | GF(L0) | DX-PAC | 18.5 TR | Schneider PAC | 100% | 100% | 80% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.177 | PAC-T6-L0-TRN1-2 | ROK | Mechanical | GF(L0) | DX-PAC | 18.5 TR | Schneider PAC | 100% | 100% | 80% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.178 | PAC-T6-L0-TRN2-1 | FOK | Mechanical | GF(L0) | DX-PAC | 18.5 TR | Schneider PAC | 100% | 100% | 100% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.179 | PAC-T6-L0-TRN2-2 | ROK | Mechanical | GF(L0) | DX-PAC | 18.5 TR | Schneider PAC | 100% | 100% | 100% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.180 | PAC-T6-L0-TRN3-1 | ROK | Mechanical | GF(L0) | DX-PAC | 18.5 TR | Schneider PAC | 100% | 100% | 100% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.181 | PAC-T6-L0-TRN3-2 | ROK | Mechanical | GF(L0) | DX-PAC | 18.5 TR | Schneider PAC | 100% | 100% | 100% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.182 | PAC-T6-L0-TRN4-1 | ROK | Mechanical | GF(L0) | DX-PAC | 18.5 TR | Schneider PAC | 100% | 100% | 100% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.183 | PAC-T6-L0-TRN4-2 | ROK | Mechanical | GF(L0) | DX-PAC | 18.5 TR | Schneider PAC | 100% | 100% | 100% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.184 | PAC-T6-L0-TRN9-1 | FOK | Mechanical | GF(L0) | DX-PAC | 27 TR | Schneider PAC | 100% | 100% | 100% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.185 | PAC-T6-L0-TRN9-2 | ROK | Mechanical | GF(L0) | DX-PAC | 27 TR | Schneider PAC | 100% | 100% | 100% | 100% | 80% | 0% | 0% | 0% | 0% | 0% | Pressure Testing Vaccum Completed
M.186 | PAC-T6-L0-TRN10-1 | ROK | Mechanical | GF(L0) | DX-PAC | 18.5 TR | Schneider PAC | 100% | 100% | 100% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.187 | PAC-T6-L0-TRN10-2 | ROK | Mechanical | GF(L0) | DX-PAC | 18.5 TR | Schneider PAC | 100% | 100% | 100% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.188 | PAC-T6-L0-TRN11-1 | ROK | Mechanical | GF(L0) | DX-PAC | 10 TR | Schneider PAC | 100% | 100% | 100% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.189 | PAC-T6-L0-TRN11-2 | FOK | Mechanical | GF(L0) | DX-PAC | 10 TR | Schneider PAC | 100% | 100% | 100% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.190 | PAC-T6-L0-HT PNL 1-1 | FOK | Mechanical | GF(L0) | DX-PAC | 3 TR | Schneider PAC | 100% | 100% | 100% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.191 | PAC-T6-L0-HT PNL 1-2 | ROK | Mechanical | GF(L0) | DX-PAC | 3 TR | Schneider PAC | 100% | 100% | 100% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.192 | PAC-T6-L0-HT PNL 2-1 | ROK | Mechanical | GF(L0) | DX-PAC | 3 TR | Schneider PAC | 100% | 100% | 100% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.193 | PAC-T6-L0-HT PNL 2-2 | ROK | Mechanical | GF(L0) | DX-PAC | 3 TR | Schneider PAC | 100% | 100% | 100% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.194 | PAC-T7-L0-TRN1-1 | ROK | Mechanical | GF(L0) | DX-PAC | 18.5 TR | Schneider PAC | 100% | 100% | 100% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.195 | PAC-T7-L0-TRN1-2 | ROK | Mechanical | GF(L0) | DX-PAC | 18.5 TR | Schneider PAC | 100% | 100% | 100% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.196 | PAC-T7-L0-TRN2-1 | ROK | Mechanical | GF(L0) | DX-PAC | 18.5 TR | Schneider PAC | 100% | 100% | 50% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.197 | PAC-T7-L0-TRN2-2 | ROK | Mechanical | GF(L0) | DX-PAC | 18.5 TR | Schneider PAC | 100% | 100% | 50% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.198 | PAC-T7-L0-TRN4-1 | ROK | Mechanical | GF(L0) | DX-PAC | 10 TR | Schneider PAC | 100% | 100% | 100% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.199 | PAC-T7-L0-TRN4-2 | ROK | Mechanical | GF(L0) | DX-PAC | 10 TR | Schneider PAC | 100% | 100% | 100% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.200 | PAC-T7-L0-TRN5-1 | ROK | Mechanical | GF(L0) | DX-PAC | 18.5 TR | Schneider PAC | 100% | 100% | 100% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.201 | PAC-T7-L0-TRN5-2 | ROK | Mechanical | GF(L0) | DX-PAC | 18.5 TR | Schneider PAC | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | RAT sensor failure scenerio pending, secondary power sources verification, BMS Report pending
M.202 | PAC-T7-L0-TRN6-1 | ROK | Mechanical | GF(L0) | DX-PAC | 27 TR | Schneider PAC | 100% | 100% | 99% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.203 | PAC-T7-L0-TRN6-2 | ROK | Mechanical | GF(L0) | DX-PAC | 27 TR | Schneider PAC | 100% | 100% | 99% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | Pressure Testing Vaccum pending
M.204 | PAC-T7-L0-TRN7-1 | ROK | Mechanical | GF(L0) | DX-PAC | 10 TR | Schneider PAC | 100% | 100% | 100% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.205 | PAC-T7-L0-TRN7-2 | ROK | Mechanical | GF(L0) | DX-PAC | 10 TR | Schneider PAC | 100% | 100% | 100% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.206 | PAC-T7-L0-TRN8-1 | ROK | Mechanical | GF(L0) | DX-PAC | 27 TR | Schneider PAC | 100% | 100% | 99% | 100% | 95% | 0% | 0% | 0% | 0% | 0%
M.207 | PAC-T7-L0-TRN8-2 | ROK | Mechanical | GF(L0) | DX-PAC | 27 TR | Schneider PAC | 100% | 80% | 0% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Pressure testing and Vaccuming is pending.
M.208 | PAC-T7-L0-TRN9-1 | ROK | Mechanical | GF(L0) | DX-PAC | 27 TR | Schneider PAC | 100% | 100% | 100% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Pressure Testing Vaccum pending
M.209 | PAC-T7-L0-TRN9-2 | ROK | Mechanical | GF(L0) | DX-PAC | 27 TR | Schneider PAC | 100% | 100% | 100% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Pressure Testing Vaccum pending
M.210 | PAC-T7-L0-TRN11-1 | ROK | Mechanical | GF(L0) | DX-PAC | 27 TR | Schneider PAC | 100% | 100% | 100% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.211 | PAC-T7-L0-TRN11-2 | ROK | Mechanical | GF(L0) | DX-PAC | 27 TR | Schneider PAC | 100% | 100% | 100% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.212 | PAC-T7-L0-HT PNL1-1 | ROK | Mechanical | GF(L0) | DX-PAC | 3 TR | Schneider PAC | 100% | 100% | 100% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.213 | PAC-T7-L0-HT PNL1-2 | ROK | Mechanical | GF(L0) | DX-PAC | 3 TR | Schneider PAC | 100% | 100% | 100% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.214 | PAC-T7-L0-HT PNL 2-1 | ROK | Mechanical | GF(L0) | DX-PAC | 3 TR | Schneider PAC | 100% | 100% | 100% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.215 | PAC-T7-L0-HT PNL 2-2 | ROK | Mechanical | GF(L0) | DX-PAC | 3 TR | Schneider PAC | 100% | 100% | 100% | 100% | 95% | 0% | 0% | 0% | 0% | 0% | Secondary power source failure pending, BMS report report not submitted
M.216 | TES Tank 1 | ROK | Mechanical | Terrace | TES | 46 KL | Shinryo Suvidha | x | 100% | 90% | 100% | x | x | x | x | x | x | Drain line drawing required. Drainpipes observed rusted condition. Some of the bolts off valve rusted, need to paint properly.
M.217 | TES Tank 2 | ROK | Mechanical | Terrace | TES | 46 KL | Shinryo Suvidha | x | 100% | 90% | 100% | x | x | x | x | x | x | Drain line drawing required. Drainpipes observed rusted condition. Some of the bolts off valve rusted, need to paint properly.
M.218 | TES Tank 3 | ROK | Mechanical | Terrace | TES | 46 KL | Shinryo Suvidha | x | 100% | 90% | 100% | x | x | x | x | x | x | Drain line drawing required. Drainpipes observed rusted condition. Some of the bolts off valve rusted, need to paint properly.
M.219 | TES Tank 4 | ROK | Mechanical | Terrace | TES | 46 KL | Shinryo Suvidha | x | 100% | 90% | 100% | x | x | x | x | x | x | Drain line drawing required. Drainpipes observed rusted condition. Some of the bolts off valve rusted, need to paint properly.
M.220 | TES Tank 5 | ROK | Mechanical | Terrace | TES | 46 KL | Shinryo Suvidha | x | 100% | 90% | 100% | x | x | x | x | x | x | Drain line drawing required. Drainpipes observed rusted condition. Some of the bolts off valve rusted, need to paint properly.
M.221 | TES Tank 6 | ROK | Mechanical | Terrace | TES | 46 KL | Shinryo Suvidha | x | 100% | 90% | 100% | x | x | x | x | x | x | Drain line drawing required. Drainpipes observed rusted condition. Some of the bolts off valve rusted, need to paint properly.
M.222 | TES Tank 7 | ROK | Mechanical | Terrace | TES | 46 KL | Shinryo Suvidha | x | 100% | 90% | 100% | x | x | x | x | x | x | Drain line drawing required. Drainpipes observed rusted condition. Some of the bolts off valve rusted, need to paint properly.
M.223 | TES Tank 8 | ROK | Mechanical | Terrace | TES | 46 KL | Shinryo Suvidha | x | 100% | 90% | 100% | x | x | x | x | x | x | Drain line drawing required. Drainpipes observed rusted condition. Some of the bolts off valve rusted, need to paint properly.
M.224 | TES Tank 9 | ROK | Mechanical | Terrace | TES | 46 KL | Shinryo Suvidha | x | 100% | 90% | 100% | x | x | x | x | x | x | Drain line drawing required. Drainpipes observed rusted condition. Some of the bolts off valve rusted, need to paint properly.
M.225 | TES Tank 10 | ROK | Mechanical | Terrace | TES | 46 KL | Shinryo Suvidha | x | 100% | 90% | 100% | x | x | x | x | x | x | Drain line drawing required. Drainpipes observed rusted condition. Some of the bolts off valve rusted, need to paint properly.
M.226 | TES Tank 11 | ROK | Mechanical | Terrace | TES | 46 KL | Shinryo Suvidha | x | 100% | 90% | 100% | x | x | x | x | x | x | Drain line drawing required. Drainpipes observed rusted condition. Some of the bolts off valve rusted, need to paint properly.
M.227 | TES Tank 12 | ROK | Mechanical | Terrace | TES | 46 KL | Shinryo Suvidha | x | 100% | 90% | 100% | x | x | x | x | x | x | Drain line drawing required. Drainpipes observed rusted condition. Some of the bolts off valve rusted, need to paint properly.
M.228 | TES Tank 13 | ROK | Mechanical | Terrace | TES | 46 KL | Shinryo Suvidha | x | 100% | 90% | 100% | x | x | x | x | x | x | Drain line drawing required. Drainpipes observed rusted condition. Some of the bolts off valve rusted, need to paint properly.
M.229 | TES Tank 14 | ROK | Mechanical | Terrace | TES | 46 KL | Shinryo Suvidha | x | 100% | 90% | 100% | x | x | x | x | x | x | Drain line drawing required. Drainpipes observed rusted condition. Some of the bolts off valve rusted, need to paint properly.
M.230 | TES Tank 15 | ROK | Mechanical | Terrace | TES | 46 KL | Shinryo Suvidha | x | 100% | 90% | 100% | x | x | x | x | x | x | Drain line drawing required. Drainpipes observed rusted condition. Some of the bolts off valve rusted, need to paint properly.
M.231 | TES Tank 16 | ROK | Mechanical | Terrace | TES | 46 KL | Shinryo Suvidha | x | 100% | 90% | 100% | x | x | x | x | x | x | Drain line drawing required. Drainpipes observed rusted condition. Some of the bolts off valve rusted, need to paint properly.
M.232 | TES Tank 17 | ROK | Mechanical | Terrace | TES | 46 KL | Shinryo Suvidha | x | 100% | 90% | 100% | x | x | x | x | x | x | Drain line drawing required. Drainpipes observed rusted condition. Some of the bolts off valve rusted, need to paint properly.
M.233 | TES Tank 18 | ROK | Mechanical | Terrace | TES | 46 KL | Shinryo Suvidha | x | 100% | 90% | 100% | x | x | x | x | x | x | Drain line drawing required. Drainpipes observed rusted condition. Some of the bolts off valve rusted, need to paint properly.
M.234 | TES Tank 19 | ROK | Mechanical | Terrace | TES | 46 KL | Shinryo Suvidha | x | 100% | 90% | 100% | x | x | x | x | x | x | Drain line drawing required. Drainpipes observed rusted condition. Some of the bolts off valve rusted, need to paint properly.
M.235 | TES Tank 20 | ROK | Mechanical | Terrace | TES | 46 KL | Shinryo Suvidha | x | 100% | 90% | 100% | x | x | x | x | x | x | Drain line drawing required. Drainpipes observed rusted condition. Some of the bolts off valve rusted, need to paint properly.
M.236 | TES Tank 21 | ROK | Mechanical | Terrace | TES | 46 KL | Shinryo Suvidha | x | 100% | 90% | 100% | x | x | x | x | x | x | Drain line drawing required. Drainpipes observed rusted condition. Some of the bolts off valve rusted, need to paint properly.
M.237 | TES Tank 22 | ROK | Mechanical | Terrace | TES | 46 KL | Shinryo Suvidha | x | 100% | 90% | 100% | x | x | x | x | x | x | Drain line drawing required. Drainpipes observed rusted condition. Some of the bolts off valve rusted, need to paint properly.
M.238 | TES Tank 23 | ROK | Mechanical | Terrace | TES | 46 KL | Shinryo Suvidha | x | 100% | 90% | 100% | x | x | x | x | x | x | Drain line drawing required. Drainpipes observed rusted condition. Some of the bolts off valve rusted, need to paint properly.
M.239 | TES Tank 24 | ROK | Mechanical | Terrace | TES | 46 KL | Shinryo Suvidha | x | 100% | 90% | 100% | x | x | x | x | x | x | Drain line drawing required. Drainpipes observed rusted condition. Some of the bolts off valve rusted, need to paint properly.
M.240 | Chiller SOO | ROK | Mechanical | - | Chiller SOO | - | - | x | x | x | x | x | x | x | 0% | 0% | 0%
M.244 | Mechanical SOO (FWU) | ROK | Mechanical | - | Mechanical SOO | - | - | x | x | x | x | x | x | x | 0% | 0% | 0%
M.245 | CDS 1 | FOK | Mechanical | Terrace | Chemical Dosing | - | Shinryo Suvidha | x | 100% | 100% | 0% | x | x | x | x | x | x
M.246 | CDS 2 | ROK | Mechanical | Terrace | Chemical Dosing | - | Shinryo Suvidha | x | 100% | 100% | 0% | x | x | x | x | x | x
M.247 | CDS 3 | ROK | Mechanical | Terrace | Chemical Dosing | - | CDVL | x | 100% | 100% | 0% | x | x | x | x | x | x | Revised TDS is not available,
M.248 | CDS 4 | ROK | Mechanical | Terrace | Chemical Dosing | - | CDVL | x | 100% | 100% | 0% | x | x | x | x | x | x | Revised TDS is not available,
M.249 | CHW Pressure test (Aux) | ROK | Mechanical | 7F, TF | Auxillary CHW Line | - | CDVL | x | 100% | 100% | x | x | x | x | x | x | x
M.250 | CHW Flushing test (Aux) | ROK | Mechanical | 7F, TF | Auxillary CHW Line | - | CDVL | x | 100% | 100% | x | x | x | x | x | x | x
M.251 | CHW TAB (Aux) | ROK | Mechanical | 7F, TF | Auxillary CHW Line | - | CDVL | x | x | x | x | 0% | 0% | x | x | x | x
M.252 | CHW Pressure test (IT) | ROK | Mechanical | 7F, TF | IT CHW Pipe Line | - | CDVL/Shinryo Suvidha | x | 100% | 100% | x | x | x | x | x | x | x
M.253 | CHW Flushing Test (IT) | ROK | Mechanical | 7F, TF | IT CHW Pipe Line | - | CDVL/Shinryo Suvidha | x | 100% | 100% | x | x | x | x | x | x | x
M.254 | CHW TAB (IT) | ROK | Mechanical | 7F, TF | IT CHW Pipe Line | - | CDVL/Shinryo Suvidha | x | x | x | x | 0% | 0% | x | x | x | x
M.256 | LC Flushing | ROK | Mechanical | 7F | Liquid Cool Flushing | - | CDVL | x | 0% | 0% | x | x | x | x | x | x | x
M.257 | LC TAB | ROK | Mechanical | 7F | Liquid Cool Water Balancing | - | CDVL | x | x | x | x | 0% | 0% | x | x | x | x
M.258 | Fuel Polishing | ROK | HSD | HSD Yard | Fuel Polishing | - | GMMCO | x | 30% | 0% | x | x | x | x | x | x | x
M.259 | Fuel Pressure test | ROK | HSD | HSD Yard | HSD | - | GMMCO | x | 60% | 0% | x | x | x | x | x | x | x

## Lists (hidden)
Equipment Type | Service | FOK/ROK | Add new Equipment Types / Services here — dropdowns and the Summary pick them up automatically.
AIS Extension Switchboard | BMS | FOK
ATS | ELV | ROK
Air Cooled Chiller | Electrical
BMS RIO | Fire
BMS System | HSD
CDU | Mechanical
CPM PLC
CPM RIO
Chemical Dousing System
DG
DG Isolator Panel
DX-PAC
Diesel Driven Pump
Dry type transformer
FAS
FCU
FWU
Fuel Leak Detection
Fuel Polishing Unit
Fuel Transfer Pump
Fuel Unloading Pump
GIS Extension Switchboard
Gas Supression System
HSD Automation System
HT Panel
Hydrant Jockey Pump
LC WLD
LT Panel
Linear Heat Detection
Main Hydrant Pump
Main Sprinkler Pump
ODU
PAHU
PAS
PDU
Preaction System
Pressure Transmiter
Pressurisation Pump
Quick Fill Pump
RMU
RPP
Return Tank Pump/Over
Rodent Repellent System
SFN
Secondary Chillwater Pump
Smoke Exhaust Fan
Sprinkler Jockey Pump
TES
TFA
Transfer Fan
UPS
Under Ground Tank
Ventilation Fan
Vesda
WLD
Water Mist System
BBT Route
Earthing

## Add. Equipment (hidden)
Equipments Removed from COLP01 to be added in COLP02
Sl. No. | Equipment ID | FOK/ROK | Service | Location | Type | Capacity | Resposible Vendor | Level 1 Report | Level 2 Test | L2 Report | L2 Tag | Level 3 Startup | L3 Report | L3 Tag | Level 4 FPT | Level 4 Report | L4 Tag | Remarks
E.009 | T6T7-RMU-7 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | relay and analog signal is pending in BMS
E.010 | T6T7-RMU-8 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | relay and analog signal is pending in BMS
E.011 | T6T7-RMU-9 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | relay and analog signal is pending in BMS
E.012 | T6T7-RMU-10 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 80% | 100% | 50% | 0% | 0% | x | x | x | relay and analog signal is pending in BMS
E.013 | T6T7-RMU-11 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 80% | 100% | 50% | 0% | 0% | x | x | x | relay and analog signal is pending in BMS
E.014 | T6T7-RMU-12 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 80% | 100% | 50% | 0% | 0% | x | x | x | relay and analog signal is pending in BMS
E.015 | T6T7-RMU-13 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 80% | 100% | 50% | 0% | 0% | x | x | x | relay and analog signal is pending in BMS
E.016 | T6T7-RMU-14 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 80% | 100% | 50% | 0% | 0% | x | x | x | relay and analog signal is pending in BMS
E.017 | T6T7-RMU-16 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 80% | 100% | 0% | 0% | 0% | x | x | x
E.019 | T6T7-RMU-18 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 80% | 100% | 0% | 0% | 0% | x | x | x
E.020 | T6T7-RMU-21 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x | relay and analog signal is pending in BMS
E.021 | T6T7-RMU-22 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x | relay and analog signal is pending in BMS
E.022 | T6T7-RMU-23 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x | relay and analog signal is pending in BMS
E.023 | T6T7-RMU-24 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 100% | 100% | 0% | 0% | 0% | x | x | x | relay and analog signal is pending in BMS
E.024 | T6T7-RMU-25 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 100% | 100% | 50% | 0% | 0% | x | x | x | relay and analog signal is pending in BMS
E.025 | T6T7-RMU-26 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 80% | 100% | 50% | 0% | 0% | x | x | x | relay and analog signal is pending in BMS
E.026 | T6T7-RMU-27 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 80% | 100% | 50% | 0% | 0% | x | x | x | relay and analog signal is pending in BMS
E.027 | T6T7-RMU-28 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 80% | 100% | 50% | 0% | 0% | x | x | x | relay and analog signal is pending in BMS
E.028 | T6T7-RMU-30 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 80% | 100% | 50% | 0% | 0% | x | x | x | relay and analog signal is pending in BMS
E.029 | T6T7-RMU-31 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 80% | 100% | 50% | 0% | 0% | x | x | x | relay and analog signal is pending in BMS
E.030 | T6T7-RMU-32 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 80% | 100% | 50% | 0% | 0% | x | x | x | relay and analog signal is pending in BMS
E.033 | T6T7-RMU-37 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 100% | 100% | 80% | 100% | 50% | 0% | 0% | x | x | x | relay and analog signal is pending in BMS
E.034 | T6T7-RMU-40 | ROK | Electrical | GF(L0) | RMU | 22kV | Siemens | 100% | 100% | 80% | 100% | 50% | 0% | 0% | x | x | x | relay and analog signal is pending in BMS
E.035 | T6T7-RMU-41 | ROK | Electrical | GF(L0) | RMU | 22kV | Siemens | 100% | 100% | 80% | 100% | 50% | 0% | 0% | x | x | x | relay and analog signal is pending in BMS
E.037 | T6T7-RMU-44 | ROK | Electrical | GF(L0) | RMU | 22kV | Siemens | 100% | 100% | 80% | 100% | 50% | 0% | 0% | x | x | x | relay and analog signal is pending in BMS
E.038 | T6T7-RMU-45 | ROK | Electrical | GF(L0) | RMU | 22kV | Siemens | 100% | 100% | 80% | 100% | 50% | 0% | 0% | x | x | x | relay and analog signal is pending in BMS
E.039 | T6T7-RMU-48 | ROK | Electrical | GF(L0) | RMU | 22kV | Siemens | 100% | 100% | 80% | 100% | 50% | 0% | 0% | x | x | x | relay and analog signal is pending in BMS
E.040 | T6T7-RMU-49 | ROK | Electrical | GF(L0) | RMU | 22kV | Siemens | 100% | 100% | 80% | 100% | 50% | 0% | 0% | x | x | x | relay and analog signal is pending in BMS
E.041 | T6T7-RMU-50 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 50% | 100% | 80% | 100% | 50% | 0% | 0% | x | x | x | relay and analog signal is pending in BMS
E.042 | T6T7-RMU-51 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 50% | 100% | 80% | 100% | 50% | 0% | 0% | x | x | x | relay and analog signal is pending in BMS
E.043 | T6T7-RMU-52 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 50% | 100% | 80% | 100% | 50% | 0% | 0% | x | x | x | relay and analog signal is pending in BMS
E.044 | T6T7-RMU-53 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 50% | 100% | 80% | 100% | 50% | 0% | 0% | x | x | x | relay and analog signal is pending in BMS
E.045 | T6T7-RMU-55 | ROK | Electrical | GF(L0) | RMU | 22kV | ABB | 50% | 90% | 80% | 0% | 0% | 0% | 0% | x | x | x | relay and analog signal is pending in BMS
E.046 | Master MCCP | ROK | Electrical | L8 | MCCP | 240V | ABB | 0% | 90% | 0% | 0% | 0% | 0% | 0% | x | x | x
Fuel Polishing Unit
Pressure monitoring System | Added as part of Preaction System in COLP01
F.179 | WMS- T6T7-DG-RISER-2 | ROK | Fire | DG Stack Area | Water Mist System | - | Fogtech | x | 0% | 0% | 0% | 0% | 0% | 0% | x | x | x
F.150 | Chiller RIO Panel -09 | ROK | ELV | TF(L9) | CPM RIO | - | Mitsubishi | x | 0% | 0% | 0% | 0% | 0% | 0% | x | x | x
F.151 | Chiller RIO Panel -10 | ROK | ELV | TF(L9) | CPM RIO | - | Mitsubishi | x | 0% | 0% | 0% | 0% | 0% | 0% | x | x | x
F.152 | Chiller RIO Panel -11 | ROK | ELV | TF(L9) | CPM RIO | - | Mitsubishi | x | 0% | 0% | 0% | 0% | 0% | 0% | x | x | x
F.153 | Chiller RIO Panel -12 | ROK | ELV | TF(L9) | CPM RIO | - | Mitsubishi | x | 0% | 0% | 0% | 0% | 0% | 0% | x | x | x
F.154 | Chiller RIO Panel -17 | ROK | ELV | TF(L9) | CPM RIO | - | Mitsubishi | x | 0% | 0% | 0% | 0% | 0% | 0% | x | x | x
F.155 | Chiller RIO Panel -18 | ROK | ELV | TF(L9) | CPM RIO | - | Mitsubishi | x | 0% | 0% | 0% | 0% | 0% | 0% | x | x | x
F.156 | Chiller RIO Panel -19 | ROK | ELV | TF(L9) | CPM RIO | - | Mitsubishi | x | 0% | 0% | 0% | 0% | 0% | 0% | x | x | x
F.157 | Chiller RIO Panel -20 | ROK | ELV | TF(L9) | CPM RIO | - | Mitsubishi | x | 0% | 0% | 0% | 0% | 0% | 0% | x | x | x
M.202 | PAC-T6-L0-TRN5-1 | ROK | Mechanical | GF(L0) | DX-PAC | 18.5 TR | Schneider PAC | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
M.203 | PAC-T6-L0-TRN5-2 | ROK | Mechanical | GF(L0) | DX-PAC | 18.5 TR | Schneider PAC | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
M.204 | PAC-T6-L0-TRN6-1 | ROK | Mechanical | GF(L0) | DX-PAC | 27 TR | Schneider PAC | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
M.205 | PAC-T6-L0-TRN6-2 | ROK | Mechanical | GF(L0) | DX-PAC | 27 TR | Schneider PAC | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
M.206 | PAC-T6-L0-TRN7-1 | ROK | Mechanical | GF(L0) | DX-PAC | 18.5 TR | Schneider PAC | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
M.207 | PAC-T6-L0-TRN7-2 | ROK | Mechanical | GF(L0) | DX-PAC | 18.5 TR | Schneider PAC | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
M.208 | PAC-T6-L0-TRN8-1 | ROK | Mechanical | GF(L0) | DX-PAC | 18.5 TR | Schneider PAC | 100% | 20% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
M.209 | PAC-T6-L0-TRN8-2 | ROK | Mechanical | GF(L0) | DX-PAC | 18.5 TR | Schneider PAC | 100% | 20% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
M.216 | PAC-T6-L0-TRN12-1 | ROK | Mechanical | GF(L0) | DX-PAC | 27 TR | Schneider PAC | 100% | 20% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
M.217 | PAC-T6-L0-TRN12-2 | ROK | Mechanical | GF(L0) | DX-PAC | 27 TR | Schneider PAC | 100% | 10% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
M.218 | PAC-T6-L0-TRN13-1 | ROK | Mechanical | GF(L0) | DX-PAC | 18.5 TR | Schneider PAC | 100% | 20% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
M.219 | PAC-T6-L0-TRN13-2 | ROK | Mechanical | GF(L0) | DX-PAC | 18.5 TR | Schneider PAC | 100% | 20% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
M.220 | PAC-T6-L0-TRN14-1 | ROK | Mechanical | GF(L0) | DX-PAC | 18.5 TR | Schneider PAC | 100% | 20% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
M.221 | PAC-T6-L0-TRN14-2 | ROK | Mechanical | GF(L0) | DX-PAC | 18.5 TR | Schneider PAC | 100% | 30% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
M.230 | PAC-T7-L0-TRN3-1 | ROK | Mechanical | GF(L0) | DX-PAC | 10 TR | Schneider PAC | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
M.231 | PAC-T7-L0-TRN3-2 | ROK | Mechanical | GF(L0) | DX-PAC | 10 TR | Schneider PAC | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
M.244 | PAC-T7-L0-TRN10-1 | ROK | Mechanical | GF(L0) | DX-PAC | 18.5 TR | Schneider PAC | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
M.245 | PAC-T7-L0-TRN10-2 | ROK | Mechanical | GF(L0) | DX-PAC | 18.5 TR | Schneider PAC | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
M.248 | PAC-T7-L0-TRN12-1 | ROK | Mechanical | GF(L0) | DX-PAC | 27 TR | Schneider PAC | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
M.249 | PAC-T7-L0-TRN12-2 | ROK | Mechanical | GF(L0) | DX-PAC | 27 TR | Schneider PAC | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
M.278 | TF- CDS -01- Primary CHWL | FOK | Mechanical | Terrace | CDS | - | Shinryo Suvidha | x | 0% | 0% | 0% | 0% | 0% | 0% | x | x | x | to be added in COLP01 itself
M.279 | TF- CDS -01- Primary CHWL | ROK | Mechanical | Terrace | CDS | - | Shinryo Suvidha | x | 0% | 0% | 0% | 0% | 0% | 0% | x | x | x | to be added in COLP01 itself
M.280 | TF-CDS-01 - Ancillary CHWL | ROK | Mechanical | Terrace | CDS | - | Shinryo Suvidha | x | 0% | 0% | 0% | 0% | 0% | 0% | x | x | x | to be added in COLP01 itself
M.281 | TF-CDS-0 - Ancillary CHWL | ROK | Mechanical | Terrace | CDS | - | Shinryo Suvidha | x | 0% | 0% | 0% | 0% | 0% | 0% | x | x | x | to be added in COLP01 itself